## Sheet2
Software Tag | Description | Connection Type | Default BOM Tag
ActvScn | Active Scene | MV
AfddTestMd | Automated Fault Detection and Diagnostics Test Mode | DV
AhuAlm | Air Handling Unit Alarm | DI
AhuAlm | Air Handling Unit Alarm | DV
AhuAlmInh | Air Handling Unit Alarm Inhibit | DV
AhuCdTmp | Air Handling Unit Cold Deck Temperature | AI
AhuCdTmp | Air Handling Unit Cold Deck Temperature | AV
AhuCdTmpSpt | Air Handling Unit Cold Deck Temperature Setpoint | AV
AhuCldEna | Air Handling Unit Cooldown Enable | DV
AhuCldTmpSpt | Air Handling Unit Cooldown Supply Temperature Setpoint | AV
AhuClgEna | Air Handling Unit Cooling Enable | DV
AhuEaFanKwh | Air Handling Unit Exhaust Fan Kilowatt-Hours | AI
AhuEaFanKwh | Air Handling Unit Exhaust Fan Kilowatt-Hours | AV
AhuEaFanSts | Air Handling Unit Exhaust Air Fan Status | DI
AhuEaFanSts | Air Handling Unit Exhaust Air Fan Status | DV
AhuHdTmp | Air Handling Unit Hot Deck Temperature | AI
AhuHdTmp | Air Handling Unit Hot Deck Temperature | AV
AhuHdTmpSpt | Air Handling Unit Hot Deck Temperature Setpoint | AV
AhuHrRTmp | Air Handling Unit Heat Recovery Return Water Temperature | AI
AhuHrRTmp | Air Handling Unit Heat Recovery Return Water Temperature | AV
AhuHtgEna | Air Handling Unit Heating Enable | DV
AhuHvacMd | Air Handling Unit HVAC Mode | MV
AhuOaDprPos | Air Handling Unit Outside Air Damper Position | AV
AhuOccSts | Air Handling Unit Occupancy Status | MV
AhuRaDprPos | Air Handling Unit Return Air Damper Position | AV
AhuRaFanKwh | Air Handling Unit Return Fan Kilowatt-Hours | AI
AhuRaFanKwh | Air Handling Unit Return Fan Kilowatt-Hours | AV
AhuSaFanKwh | Air Handling Unit Supply Fan Kilowatt-Hours | AI
AhuSaFanKwh | Air Handling Unit Supply Fan Kilowatt-Hours | AV
AhuSaFanSts | Air Handling Unit Supply Air Fan Status | DI
AhuSaFanSts | Air Handling Unit Supply Air Fan Status | DV
AhuSaTmp | Air Handling Unit Supply Air Temperature | AI
AhuSaTmp | Air Handling Unit Supply Air Temperature | AV
AhuSaTmpSpt | Air Handling Unit Supply Air Temperature Setpoint | AV
AhuSbEna | Air Handling Unit Setback Enable | DV
AhuWu | Air Handling Unit Warmup | DV
AhuWuDif | Air Handling Unit Warmup Differential | AV
AhuWuDof | Air Handling Unit Warmup Delay Off | AV
AhuWuEna | Air Handling Unit Warmup Enable | DV
AhuWuOfs | Air Handling Unit Warmup Offset | AV
AhuWuTmpSpt | Air Handling Unit Warmup Temperature Set Point | AV
AirFl | Air Flow | AI
AirFl | Air Flow | AV
AirFl | Air Flow | PNEU
AirFlBalMd | Air Flow Balance Mode | MV
AirFlCalAlm | Air Flow Calibration Alarm | DV
AirFlCalAlmSv | Air Flow Calibration Alarm Shunt Variable | DV
AirFlFalm | Air Flow Fail Alarm | DV
AirFlHalm | Air Flow High Alarm | DV
AirFlLalm | Air Flow Low Alarm | DV
AirFlLalmSv | Air Flow Low Alarm Shunt Variable | DV
AirFlLoWrn | Air Flow Low Warning | DV
AirFlLoWrnSv | Air Flow Low Warning Shunt Variable | DV
AirFlMaxTestSts | Maximum Air Flow Test Status | MV
AirFlMinTestSts | Minimum Air Flow Test Status | MV
AirFlSpt | Air Flow Setpoint | AV
AirFlSptClgMax | Maximum Cooling Air Flow Setpoint | AV
AirFlSptClgMid | Intermediate Cooling Air Flow Setpoint | AV
AirFlSptClgMin | Minimum Cooling Air Flow Setpoint | AV
AirFlSptHtgMax | Maximum Heating Air Flow Setpoint | AV
AirFlSptHtgMid | Intermediate Heating Air Flow Setpoint | AV
AirFlSptHtgMin | Minimum Heating Air Flow Setpoint | AV
AirFlSptMax | Maximum Air Flow Setpoint | AV
AirFlSptMid | Intermediate Air Flow Setpoint | AV
AirFlSptMin | Minimum Air Flow Setpoint | AV
AirFlSptMinBldg | Minimum Air Flow Setpoint for Building | AV
AirFlSptMinBldgEff | Minimum Effective Air Flow Setpoint for Building | AV
AirFlSptMinOcc | Minimum Air Flow Setpoint for Occupancy | AV
AirFlSptMinOccEff | Minimum Effective Air Flow Setpoint for Occupancy | AV
AirFlSptMinUnoc | Minimum Unoccupied Air Flow Setpoint | AV
AirFlSptVntEna | Air Flow Minimum Outside Air Ventilation Enable | DV
AirFlSptVntMin | Air Flow Minimum Outside Air Ventilation Setpoint | AV
AirFlTestMd | Air Flow Test Mode | MV
AlmInhAlm | Alarm Inhibit Alarm | DV
AlmInhAlmChw | Alarm Inhibit Alarm for Chilled Water System | DV
AlmInhAlmCw | Alarm Inhibit Alarm for Condenser Water System | DV
AlmInhAlmHw | Alarm Inhibit Alarm for Hot Water System | DV
AlmInhChw | Alarm Inhibit for Chilled Water System | DV
AlmInhCw | Alarm Inhibit for Condenser Water System | DV
AlmInhHw | Alarm Inhibit for Hot Water System | DV
AlmSig | Alarm Signal | DI
AlmSig | Alarm Signal | DV
AlmSigAlm | Alarm Signal Alarm | DV
AmbLux | Ambient Illuminance | AI
AmbLux | Ambient Illuminance | AV
AmbLuxMax | Maximum Ambient Illuminance | AV
AnyChIsoVlvEsw | Any Chiller Isolation Valve End Switch | DV
AnyOcc | Any Occupancy | DV
AnyOvr | Any Override | DV
AnyPchwPSts | Any Primary Chilled Water Pump Status | DV
AnySchwPSts | Any Secondary Chilled Water Pump Status | DV
AnyStb | Any Standby | DV
AnyUnoc | Any Unoccupied | DV
AtsAlm | Automatic Transfer Switch Alarm | DV
AtsByp | Automatic Transfer Switch In Bypass | DV
AtsBypEmerAvl | Automatic Transfer Switch Bypass to Emergency Available | DV
AtsBypEmerConn | Automatic Transfer Switch Bypass to Emergency Connected | DV
AtsBypNormAvl | Automatic Transfer Switch Bypass to Normal Available | DV
AtsBypNormConn | Automatic Transfer Switch Bypass to Normal Connected | DV
AtsEmerPwrAvl | Automatic Transfer Switch Emergency Power Available | DV
AtsEmerPwrConn | Automatic Transfer Switch Emergency Power Connected | DV
AtsEmerPwrReq | Automatic Transfer Switch Emergency Power Request | DV
AtsNia | Automatic Transfer Switch Not In Automatic | DV
AtsNormPwrAvl | Automatic Transfer Switch Normal Power Available | DV
AtsNormPwrConn | Automatic Transfer Switch Normal Power Connected | DV
AtsTest | Automatic Transfer Switch In Test | DV
AutoCalActv | Floating Actuator Auto Calibration Active | DV
AutoCalEna | Floating Actuator Auto Calibration Enable | DV
AuxConCfg | Auxiliary Contact Configuration | MV
AuxConSts | Auxiliary Contact Status | DI
AuxConSts | Auxiliary Contact Status | DV
AuxEna | Auxiliary Enable | DV
AuxHtgCmd | Auxiliary Heating Command | DO
AuxHtgCmd | Auxiliary Heating Command | DV
AuxHtgMax | Auxiliary Heating Maximum | AV
AuxHtgMin | Auxiliary Heating Minimum | AV
AuxHtgPos | Auxiliary Heating Position | AO
AuxHtgPos | Auxiliary Heating Position | AV
AuxHtgTestMd | Auxiliary Heating Test Mode | MV
BalFlCorFct | Balanced Box Flow Correction Factor | AV
BalKFct | Balanced k-Factor | AV
BdVlvCmd | Blowdown Valve Command | DO
BdVlvCmd | Blowdown Valve Command | DV
BldgBypVlvPos | Building Bypass Valve Position | AO
BldgBypVlvPos | Building Bypass Valve Position | AV
BldgClgLoad | Building Cooling Load | AV
BldgClgLoadHlmt | Building Cooling Load High Limit | AV
BldgClgLoadLlmt | Building Cooling Load Low Limit | AV
BldgDifPr | Building Differential Pressure | AI
BldgDifPr | Building Differential Pressure | AV
BldgElecKva | Building Electrical Apparent Power | AI
BldgElecKva | Building Electrical Apparent Power | AV
BldgElecKvar | Building Electrical Energy | AI
BldgElecKvar | Building Electrical Energy | AV
BldgElecKw | Building Electrical Kilowatts | AI
BldgElecKw | Building Electrical Kilowatts | AV
BldgElecKwh | Building Electrical Kilowatt-Hours | AI
BldgElecKwh | Building Electrical Kilowatt-Hours | AV
BldgGasFl | Building Gas Flow | AI
BldgGasFl | Building Gas Flow | AV
BldgHwRTmp | Building Hot Water Return Temperature | AI
BldgHwRTmp | Building Hot Water Return Temperature | AV
BldgHwSTmp | Building Hot Water Supply Temperature | AI
BldgHwSTmp | Building Hot Water Supply Temperature | AV
BldgOilFl | Building Oil Flow | AI
BldgOilFl | Building Oil Flow | AV
BldgStmFl | Building Steam Flow | AI
BldgStmFl | Building Steam Flow | AV
BldgStPr | Building Static Pressure | AI
BldgStPr | Building Static Pressure | AV
BldgStPrFalm | Building Static Pressure Fail Alarm | DV
BldgStPrFalmSv | Building Static Pressure Fail Alarm Shunt Variable | DV
BldgStPrHalm | Building Static Pressure High Alarm | DV
BldgStPrHalmSv | Building Static Pressure High Alarm Shunt Variable | DV
BldgStPrLalm | Building Static Pressure Low Alarm | DV
BldgStPrLalmSv | Building Static Pressure Low Alarm Shunt Variable | DV
BldgStPrLoad | Building Static Pressure Load | AV
BldgStPrSpt | Building Static Pressure Setpoint | AV
BldgStPrTestMd | Building Static Pressure Test Mode | MV
BldgStPrTestSts | Building Static Pressure Test Status | MV
BlrAlm | Boiler Alarm | DI
BlrAlm | Boiler Alarm | DV
BlrAmp | Boiler Amps | AI
BlrAmp | Boiler Amps | AV
BlrBrnrGasVlvPos | Boiler Burner Gas Valve Position | AO
BlrBrnrGasVlvPos | Boiler Burner Gas Valve Position | AV
BlrBypVlvFalm | Boiler Bypass Valve Failure Alarm | DV
BlrBypVlvFbk | Boiler Bypass Valve Feedback | AI
BlrBypVlvFbk | Boiler Bypass Valve Feedback | AV
BlrBypVlvPos | Boiler Bypass Valve Position | AO
BlrBypVlvPos | Boiler Bypass Valve Position | AV
BlrCapDsn | Boiler Capacity Design | AV
BlrCirPCmd | Boiler Circulation Pump Command | DO
BlrCirPCmd | Boiler Circulation Pump Command | DV
BlrCirPSts | Boiler Circulation Pump Status | DI
BlrCirPSts | Boiler Circulation Pump Status | DV
BlrCmd | Boiler Command | DO
BlrCmd | Boiler Command | DV
BlrEna | Boiler Enable | DO
BlrEna | Boiler Enable | DV
BlrFireRate | Boiler Firing Rate | AI
BlrFireRate | Boiler Firing Rate | AV
BlrFireRateMin | Boiler Minimum Firing Rate Before Cycling | AV
BlrFlSptDsn | Boiler Manufacturer Designed Flow | AV
BlrFlSptDsnMin | Boiler Manufacturer Minimum Designed Flow | AV
BlrFlueO2 | Boiler Flue Oxygen Concentration | AI
BlrFlueO2 | Boiler Flue Oxygen Concentration | AV
BlrFlueSts | Boiler Flue Status | DI
BlrFlueSts | Boiler Flue Status | DV
BlrFlueTmp | Boiler Flue Temperature | AI
BlrFlueTmp | Boiler Flue Temperature | AV
BlrFof | Boiler Fail Off Alarm | DV
BlrFon | Boiler Fail On Alarm | DV
BlrGasFl | Boiler Natural Gas Flow | AI
BlrGasFl | Boiler Natural Gas Flow | AV
BlrGasFlMain | Main Steam Boiler Gas Flow | AI
BlrGasFlMain | Main Steam Boiler Gas Flow | AV
BlrHwDifPr | Boiler Hot Water Differential Pressure | AI
BlrHwDifPr | Boiler Hot Water Differential Pressure | AV
BlrHwFl | Boiler Hot Water Flow | AI
BlrHwFl | Boiler Hot Water Flow | AV
BlrHwRFl | Boiler Hot Water Return Flow | AI
BlrHwRFl | Boiler Hot Water Return Flow | AV
BlrHwRFlSpt | Boiler Hot Water Return Flow Setpoint | AV
BlrHwRIsoVlvCmd | Boiler Hot Water Return Isolation Valve Command | DO
BlrHwRIsoVlvCmd | Boiler Hot Water Return Isolation Valve Command | DV
BlrHwRIsoVlvCmdCls | Boiler Hot Water Return Isolation Valve Close Command | DO
BlrHwRIsoVlvCmdCls | Boiler Hot Water Return Isolation Valve Close Command | DV
BlrHwRIsoVlvCmdOpn | Boiler Hot Water Return Isolation Valve Open Command | DO
BlrHwRIsoVlvCmdOpn | Boiler Hot Water Return Isolation Valve Open Command | DV
BlrHwRIsoVlvEsw | Boiler Hot Water Return Isolation Valve End Switch | DI
BlrHwRIsoVlvEsw | Boiler Hot Water Return Isolation Valve End Switch | DV
BlrHwRIsoVlvEswCls | Boiler Hot Water Return Isolation Valve Closed End Switch | DI
BlrHwRIsoVlvEswCls | Boiler Hot Water Return Isolation Valve Closed End Switch | DV
BlrHwRIsoVlvEswOpn | Boiler Hot Water Return Isolation Valve Open End Switch | DI
BlrHwRIsoVlvEswOpn | Boiler Hot Water Return Isolation Valve Open End Switch | DV
BlrHwRIsoVlvFalm | Boiler Hot Water Return Isolation Valve Failure Alarm | DV
BlrHwRIsoVlvFbk | Boiler Hot Water Return Isolation Valve Feedback | AI
BlrHwRIsoVlvFbk | Boiler Hot Water Return Isolation Valve Feedback | AV
BlrHwRIsoVlvFcls | Boiler Hot Water Return Isolation Valve Fail Closed Alarm | DV
BlrHwRIsoVlvFopn | Boiler Hot Water Return Isolation Valve Fail Open Alarm | DV
BlrHwRIsoVlvPos | Boiler Hot Water Return Isolation Valve Position | AO
BlrHwRIsoVlvPos | Boiler Hot Water Return Isolation Valve Position | AV
BlrHwRTmp | Boiler Hot Water Return Temperature | AI
BlrHwRTmp | Boiler Hot Water Return Temperature | AV
BlrHwRTmpSpt | Boiler Hot Water Return Temperature Setpoint | AV
BlrHwSFl | Boiler Hot Water Supply Flow | AI
BlrHwSFl | Boiler Hot Water Supply Flow | AV
BlrHwSFlSpt | Boiler Hot Water Supply Flow Setpoint | AV
BlrHwSIsoVlvCmd | Boiler Hot Water Supply Isolation Valve Command | DO
BlrHwSIsoVlvCmd | Boiler Hot Water Supply Isolation Valve Command | DV
BlrHwSIsoVlvCmdCls | Boiler Hot Water Supply Isolation Valve Close Command | DO
BlrHwSIsoVlvCmdCls | Boiler Hot Water Supply Isolation Valve Close Command | DV
BlrHwSIsoVlvCmdOpn | Boiler Hot Water Supply Isolation Valve Open Command | DO
BlrHwSIsoVlvCmdOpn | Boiler Hot Water Supply Isolation Valve Open Command | DV
BlrHwSIsoVlvEsw | Boiler Hot Water Supply Isolation Valve End Switch | DI
BlrHwSIsoVlvEsw | Boiler Hot Water Supply Isolation Valve End Switch | DV
BlrHwSIsoVlvEswCls | Boiler Hot Water Supply Isolation Valve Closed End Switch | DI
BlrHwSIsoVlvEswCls | Boiler Hot Water Supply Isolation Valve Closed End Switch | DV
BlrHwSIsoVlvEswOpn | Boiler Hot Water Supply Isolation Valve Open End Switch | DI
BlrHwSIsoVlvEswOpn | Boiler Hot Water Supply Isolation Valve Open End Switch | DV
BlrHwSIsoVlvFalm | Boiler Hot Water Supply Isolation Valve Failure Alarm | DV
BlrHwSIsoVlvFbk | Boiler Hot Water Supply Isolation Valve Feedback | AI
BlrHwSIsoVlvFbk | Boiler Hot Water Supply Isolation Valve Feedback | AV
BlrHwSIsoVlvFcls | Boiler Hot Water Supply Isolation Valve Fail Closed Alarm | DV
BlrHwSIsoVlvFopn | Boiler Hot Water Supply Isolation Valve Fail Open Alarm | DV
BlrHwSIsoVlvPos | Boiler Hot Water Supply Isolation Valve Position | AO
BlrHwSIsoVlvPos | Boiler Hot Water Supply Isolation Valve Position | AV
BlrHwSTmp | Boiler Hot Water Supply Temperature | AI
BlrHwSTmp | Boiler Hot Water Supply Temperature | AV
BlrHwSTmpAlm | Boiler Hot Water Supply Temperature Alarm | DV
BlrHwSTmpAlmSv | Boiler Hot Water Supply Temperature Alarm Shunt Variable | DV
BlrHwSTmpSpt | Boiler Hot Water Supply Temperature Setpoint | AV
BlrIsoVlvFbk | Boiler Isolation Valve Feedback | AI
BlrIsoVlvFbk | Boiler Isolation Valve Feedback | AV
BlrLclLoc | Boiler Local Lockout | DV
BlrLclLocRst | Boiler Local Lockout Reset | DV
BlrLd | Boiler Lead | AV
BlrLdMan | Boiler Lead Manual | AV
BlrLg | Boiler Lag | AV
BlrLgMan | Boiler Lag Manual | AV
BlrMaintMd | Boiler Maintenance Mode | DV
BlrMaintMdAlm | Boiler Maintenance Mode Alarm | DV
BlrMaintReqAlm | Boiler Maintenance Request | DV
BlrMaintReqRtRst | Boiler Maintenance Request Run Time Reset | DV
BlrNumAvl | Number of Boilers Available | AV
BlrNumHwIsoVlvOpn | Number of Boilers with Open Hot Water Isolation Valves Open | AV
BlrNumLclLoc | Number of Boilers In Local Lockout | AV
BlrNumOvrOn | Number of Boilers Which Are Overridden On | AV
BlrNumReq | Number of Boilers Request | AV
BlrNumRun | Number of Boilers Running | AV
BlrOaTmpEnaSpt | Boiler Outside Air Temperature Enable Setpoint | AV
BlrOvrOn | Boiler Overridden On | DV
BlrPCmd | Boiler Pump Command | DO
BlrPCmd | Boiler Pump Command | DV
BlrPSts | Boiler Pump Status | DI
BlrPSts | Boiler Pump Status | DV
BlrRotCmdTs | Boiler Rotation Command From Time Schedule | DV
BlrRotOrdManValid | Boiler Manual Rotation Order Valid | DV
BlrRotOrdValid | Boiler Rotation Order Valid | DV
BlrRotSel | Boiler Rotation Selection | MV
BlrRotSelfCor | Boiler Rotation Self Correcting Option | DV
BlrRotSw | Boiler Rotation Switch | DV
BlrRotTsFrcRot | Boiler Rotation Time Schedule Force Rotation Option | DV
BlrRt | Boiler Run Time | AV
BlrRTmp | Boiler Return Temperature | AI
BlrRTmp | Boiler Return Temperature | AV
BlrRtRst | Boiler Run Time Reset | DV
BlrStgActvCapDsn | Boiler Active Stage Design Capacity | AV
BlrStgActvCapMin | Boiler Active Stage Minimum Capacity | AV
BlrStgActvFlMin | Boiler Active Stage Minimum Flow | AV
BlrStgNxtCapDsn | Boiler Next Stage Design Capacity | AV
BlrStgNxtCapMin | Boiler Next Stage Minimum Capacity | AV
BlrStgNxtFlMin | Boiler Next Stage Minimum Flow | AV
BlrStgPrvCapDsn | Boiler Previous Stage Design Capacity | AV
BlrStgPrvCapMin | Boiler Previous Stage Minimum Capacity | AV
BlrStgPrvFlMin | Boiler Previous Stage Minimum Flow | AV
BlrStgSpt | Boiler Staging Setpoint | AV
BlrStmFl | Boiler Steam Flow | AI
BlrStmFl | Boiler Steam Flow | AV
BlrSTmp | Boiler Supply Temperature | AI
BlrSTmp | Boiler Supply Temperature | AV
BlrStmPr | Boiler Steam Pressure | AI
BlrStmPr | Boiler Steam Pressure | AV
BlrStmPrSpt | Boiler Steam Pressure Setpoint | AV
BlrSts | Boiler Status | DI
BlrSts | Boiler Status | DV
BlrXrt | Boiler Extended Run Time | AV
BoxFlMax | Maximum Measured Box Flow | AV
BoxFlMid | Intermediate Measured Box Flow | AV
BoxFlMin | Minimum Measured Box Flow | AV
BoxFlRated | Rated Box Flow | AV
BoxFlRatedFalm | Rated Box Flow Fail Alarm | DV
BypDprPos | Bypass Damper Position | AO
BypDprPos | Bypass Damper Position | AV
CdAhuWu | Air Handling Unit Cold Deck Warmup | DV
CdAirFl | Cold Deck Air Flow | AI
CdAirFl | Cold Deck Air Flow | AV
CdAirFl | Cold Deck Air Flow | PNEU
CdAirFlBalMd | Cold Deck Air Flow Balance Mode | MV
CdAirFlCalAlm | Cold Deck Air Flow Calibration Alarm | DV
CdAirFlCalAlmSv | Cold Deck Air Flow Calibration Alarm Shunt Variable | DV
CdAirFlFalm | Cold Deck Air Flow Fail Alarm | DV
CdAirFlHalm | Cold Deck Air Flow High Alarm | DV
CdAirFlLalm | Cold Deck Air Flow Low Alarm | DV
CdAirFlLalmSv | Cold Deck Air Flow Low Alarm Shunt Variable | DV
CdAirFlLoWrn | Cold Deck Air Flow Low Warning | DV
CdAirFlLoWrnSv | Cold Deck Air Flow Low Warning Shunt Variable | DV
CdAirFlMaxTestSts | Maximum Cold Deck Air Flow Test Status | MV
CdAirFlMinTestSts | Minimum Cold Deck Air Flow Test Status | MV
CdAirFlSpt | Cold Deck Air Flow Setpoint | AV
CdAirFlSptMax | Maximum Cold Deck Air Flow Setpoint | AV
CdAirFlSptMid | Intermediate Cold Deck Air Flow Setpoint | AV
CdAirFlSptMin | Minimum Cold Deck Air Flow Setpoint | AV
CdAirFlTestMd | Cold Deck Air Flow Test Mode | MV
CdBalFlCorFct | Cold Deck Balanced Box Flow Correction Factor | AV
CdBalKFct | Cold Deck Balanced k-Factor | AV
CdBoxFlMax | Cold Deck Maximum Measured Box Flow | AV
CdBoxFlMid | Cold Deck Intermediate Measured Box Flow | AV
CdBoxFlMin | Cold Deck Minimum Measured Box Flow | AV
CdBoxFlRated | Cold Deck Box Rated Flow | AV
CdBoxFlRatedFalm | Cold Deck Rated Box Flow Fail Alarm | DV
CdClsofTestSts | Cold Deck Close Off Test Status | MV
CdDprCmd | Cold Deck Damper Command | DO
CdDprCmd | Cold Deck Damper Command | DV
CdDprCmdCls | Cold Deck Damper Close Command | DO
CdDprCmdCls | Cold Deck Damper Close Command | DV
CdDprCmdOpn | Cold Deck Damper Open Command | DO
CdDprCmdOpn | Cold Deck Damper Open Command | DV
CdDprFbk | Cold Deck Damper Feedback | AO
CdDprFbk | Cold Deck Damper Feedback | AV
CdDprLkAlm | Cold Deck Damper Leak Alarm | DV
CdDprLkAlmSv | Cold Deck Damper Lead Alarm Shunt Variable | DV
CdDprPos | Cold Deck Damper Position | AO
CdDprPos | Cold Deck Damper Position | AV
CdDprTestMd | Cold Deck Damper Test Mode | MV
CdHoodFlMax | Cold Deck Maximum Measured Hood Flow | AV
CdHoodFlMid | Cold Deck Intermediate Measured Hood Flow | AV
CdHoodFlMin | Cold Deck Minimum Measured Hood Flow | AV
CdRatedBoxFlowFalm | Cold Deck Rated Box Flow Fail Alarm - Must Be Non-Zero | DV
CdStPr | Cold Deck Static Pressure | AI
CdStPr | Cold Deck Static Pressure | AV
CdStPrRstReq | Cold Deck Static Pressure Reset Requests | AV
CdStPrRstReqHalm | Cold Deck Static Pressure Reset Request High Alarm | DV
CdStPrRstReqHalmSv | Cold Deck Static Pressure Reset Request High Alarm Shunt Variable | DV
CdStPrRstReqPct | Cold Deck Static Pressure Reset Request Hours as Percent | AV
CdStPrRstReqRst | Cold Deck Static Pressure Reset Request Hours Reset | DV
CdStPrRstReqRt | Cold Deck Static Pressure Reset Request Hours | AV
CdTmaVntClsTml | Cold Deck Time-Averaged Close Time Left | AV
CdTmaVntOpnTml | Cold Deck Time-Averaged Open Time Left | AV
CdTmaVntSts | Cold Deck Time-Averaged Ventilation Status | DV
CdTmp | Cold Deck Temperature | AI
CdTmp | Cold Deck Temperature | AV
CdTmpAlmSv | Cold Deck Temperature Alarm Shunt Variable | DV
CdTmpFalm | Cold Deck Temperature Fail Alarm | DV
CdTmpHalm | Cold Deck Temperature High Alarm | DV
CdTmpLalm | Cold Deck Temperature Low Alarm | DV
CdTmpSpt | Cold Deck Temperature Setpoint | AV
CdVelPr | Cold Deck Velocity Pressure | AI
CdVelPr | Cold Deck Velocity Pressure | AV
CdVelPrTestSts | Cold Deck Velocity Pressure Test Stage | MV
ChAlm | Chiller Alarm | DI
ChAlm | Chiller Alarm | DV
ChAmp | Chiller Amps | AI
ChAmp | Chiller Amps | AV
ChbChwSTmp | Chilled Beam Chilled Water Supply Temperature | AI
ChbChwSTmp | Chilled Beam Chilled Water Supply Temperature | AV
ChbChwSTmpSpt | Chilled Beam Chilled Water Supply Temperature Setpoint | AI
ChbChwSTmpSpt | Chilled Beam Chilled Water Supply Temperature Setpoint | AV
ChBypVlvPos | Chiller Bypass Valve Position | AO
ChBypVlvPos | Chiller Bypass Valve Position | AV
ChChwDifPr | Chiller Chilled Water Differential Pressure | AI
ChChwDifPr | Chiller Chilled Water Differential Pressure | AV
ChChwFl | Chiller Chilled Water Flow | AI
ChChwFl | Chiller Chilled Water Flow | AV
ChChwFlSpt | Chiller Chilled Water Flow Setpoint | AV
ChChwRIsoVlvCmd | Chiller Chilled Water Return Isolation Valve Command | DO
ChChwRIsoVlvCmd | Chiller Chilled Water Return Isolation Valve Command | DV
ChChwRIsoVlvCmdCls | Chiller Chilled Water Return Isolation Valve Close Command | DO
ChChwRIsoVlvCmdCls | Chiller Chilled Water Return Isolation Valve Close Command | DV
ChChwRIsoVlvCmdOpn | Chiller Chilled Water Return Isolation Valve Open Command | DO
ChChwRIsoVlvCmdOpn | Chiller Chilled Water Return Isolation Valve Open Command | DV
ChChwRIsoVlvEsw | Chiller Chilled Water Return Isolation Valve End Switch | DI
ChChwRIsoVlvEsw | Chiller Chilled Water Return Isolation Valve End Switch | DV
ChChwRIsoVlvEswCls | Chiller Chilled Water Return Isolation Valve End Switch Closed | DI
ChChwRIsoVlvEswCls | Chiller Chilled Water Return Isolation Valve End Switch Closed | DV
ChChwRIsoVlvEswOpn | Chiller Chilled Water Return Isolation Valve End Switch Open | DI
ChChwRIsoVlvEswOpn | Chiller Chilled Water Return Isolation Valve End Switch Open | DV
ChChwRIsoVlvFcls | Chilled Water Return Isolation Valve Fail Close Alarm | DV
ChChwRIsoVlvFopn | Chilled Water Return Isolation Valve Fail Open Alarm | DV
ChChwRTmp | Chiller Chilled Water Return Temperature | AI
ChChwRTmp | Chiller Chilled Water Return Temperature | AV
ChChwRVlvFcls | Chilled Water Return Valve Fail Close Alarm | DV
ChChwRVlvFopn | Chilled Water Return Valve Fail Open Alarm | DV
ChChwSFl | Chiller Chilled Water Supply Flow | AI
ChChwSFl | Chiller Chilled Water Supply Flow | AV
ChChwSIsoVlvCmd | Chiller Chilled Water Supply Isolation Valve Command | DO
ChChwSIsoVlvCmd | Chiller Chilled Water Supply Isolation Valve Command | DV
ChChwSIsoVlvCmdCls | Chiller Chilled Water Supply Isolation Valve Close Command | DO
ChChwSIsoVlvCmdCls | Chiller Chilled Water Supply Isolation Valve Close Command | DV
ChChwSIsoVlvCmdOpn | Chiller Chilled Water Supply Isolation Valve Open Command | DO
ChChwSIsoVlvCmdOpn | Chiller Chilled Water Supply Isolation Valve Open Command | DV
ChChwSIsoVlvEsw | Chiller Chilled Water Supply Isolation Valve End Switch | DI
ChChwSIsoVlvEsw | Chiller Chilled Water Supply Isolation Valve End Switch | DV
ChChwSIsoVlvEswCls | Chiller Chilled Water Supply Isolation Valve End Switch Closed | DI
ChChwSIsoVlvEswCls | Chiller Chilled Water Supply Isolation Valve End Switch Closed | DV
ChChwSIsoVlvEswOpn | Chiller Chilled Water Supply Isolation Valve End Switch Open | DI
ChChwSIsoVlvEswOpn | Chiller Chilled Water Supply Isolation Valve End Switch Open | DV
ChChwSIsoVlvFcls | Chilled Water Supply Isolation Valve Fail Close Alarm | DV
ChChwSIsoVlvFopn | Chilled Water Supply Isolation Valve Fail Open Alarm | DV
ChChwSTmp | Chiller Chilled Water Supply Temperature | AI
ChChwSTmp | Chiller Chilled Water Supply Temperature | AV
ChChwSTmpSpt | Chiller Chilled Water Supply Temperature Setpoint | AV
ChCmd | Chiller Command | DO
ChCmd | Chiller Command | DV
ChCmdDof | Chiller Command Delay Off | AV
ChCmdDon | Chiller Command Delay On | AV
ChCmdOvrAlm | Chiller Command Forced By Operator Alarm | DV
ChCwDifPr | Chiller Condenser Water Differential Pressure | AI
ChCwDifPr | Chiller Condenser Water Differential Pressure | AV
ChCwFl | Chiller Condenser Water Flow | AI
ChCwFl | Chiller Condenser Water Flow | AV
ChCwFlSpt | Chiller Condenser Water Flow Setpoint | AV
ChCwRIsoVlvCmd | Chiller Condenser Water Return Isolation Valve Command | DO
ChCwRIsoVlvCmd | Chiller Condenser Water Return Isolation Valve Command | DV
ChCwRIsoVlvCmdCls | Chiller Condenser Water Return Isolation Valve Close Command | DO
ChCwRIsoVlvCmdCls | Chiller Condenser Water Return Isolation Valve Close Command | DV
ChCwRIsoVlvCmdOpn | Chiller Condenser Water Return Isolation Valve Open Command | DO
ChCwRIsoVlvCmdOpn | Chiller Condenser Water Return Isolation Valve Open Command | DV
ChCwRIsoVlvEsw | Chiller Condenser Water Return Isolation Valve End Switch | DI
ChCwRIsoVlvEsw | Chiller Condenser Water Return Isolation Valve End Switch | DV
ChCwRIsoVlvEswCls | Chiller Condenser Water Return Isolation Valve End Switch Closed | DI
ChCwRIsoVlvEswCls | Chiller Condenser Water Return Isolation Valve End Switch Closed | DV
ChCwRIsoVlvEswOpn | Chiller Condenser Water Return Isolation Valve End Switch Open | DI
ChCwRIsoVlvEswOpn | Chiller Condenser Water Return Isolation Valve End Switch Open | DV
ChCwRIsoVlvFcls | Chiller Condenser Water Return Isolation Valve Fail Close Alarm | DV
ChCwRIsoVlvFopn | Chiller Condenser Water Return Isolation Valve Fail Open Alarm | DV
ChCwRTmp | Chiller Condenser Water Return Temperature | AI
ChCwRTmp | Chiller Condenser Water Return Temperature | AV
ChCwRVlvFcls | Chiller Condenser Water Return Valve Fail Close Alarm | DV
ChCwRVlvFopn | Chiller Condenser Water Return Valve Fail Open Alarm | DV
ChCwSFl | Chiller Condenser Water Supply Flow | AI
ChCwSFl | Chiller Condenser Water Supply Flow | AV
ChCwSIsoVlvCmd | Chiller Condenser Water Supply Isolation Valve Command | DO
ChCwSIsoVlvCmd | Chiller Condenser Water Supply Isolation Valve Command | DV
ChCwSIsoVlvCmdCls | Chiller Condenser Water Supply Isolation Valve Close Command | DO
ChCwSIsoVlvCmdCls | Chiller Condenser Water Supply Isolation Valve Close Command | DV
ChCwSIsoVlvCmdOpn | Chiller Condenser Water Supply Isolation Valve Open Command | DO
ChCwSIsoVlvCmdOpn | Chiller Condenser Water Supply Isolation Valve Open Command | DV
ChCwSIsoVlvEsw | Chiller Condenser Water Supply Isolation Valve End Switch | DI
ChCwSIsoVlvEsw | Chiller Condenser Water Supply Isolation Valve End Switch | DV
ChCwSIsoVlvEswCls | Chiller Condenser Water Supply Isolation Valve End Switch Closed | DI
ChCwSIsoVlvEswCls | Chiller Condenser Water Supply Isolation Valve End Switch Closed | DV
ChCwSIsoVlvEswOpn | Chiller Condenser Water Supply Isolation Valve End Switch Open | DI
ChCwSIsoVlvEswOpn | Chiller Condenser Water Supply Isolation Valve End Switch Open | DV
ChCwSIsoVlvFcls | Chiller Condenser Water Supply Isolation Valve Fail Close Alarm | DV
ChCwSIsoVlvFopn | Chiller Condenser Water Supply Isolation Valve Fail Open Alarm | DV
ChCwSTmp | Chiller Condenser Water Supply Temperature | AI
ChCwSTmp | Chiller Condenser Water Supply Temperature | AV
ChDifPr | Chiller Differential Pressure | AI
ChDifPr | Chiller Differential Pressure | AV
ChDifPrSpt | Chiller Differential Pressure Setpoint | AV
ChEf | Chiller Efficiency | AV
ChElecKw | Chiller Electric Kilowatts | AV
ChElecKwh | Chiller Electric Kilowatt-Hours | AV
ChEna | Chiller Enable | DO
ChEna | Chiller Enable | DV
ChFalm | Chiller Fail Alarm | DI
ChFalm | Chiller Fail Alarm | DV
ChFl | Chiller Flow | AI
ChFl | Chiller Flow | AV
ChFlLo | Minimum Chiller Flow | AV
ChFlLoSpt | Minimum Chiller Flow Setpoint | AV
ChFlSw | Chiller Flow Switch | DI
ChFlSw | Chiller Flow Switch | DV
ChFof | Chiller Fail Off Alarm | DV
ChFon | Chiller Fail On Alarm | DV
ChgVlvCmd | Changeover Valve Command | DO
ChgVlvCmd | Changeover Valve Command | DV
ChgVlvPos | Changeover Valve Position | AO
ChgVlvPos | Changeover Valve Position | AV
ChgVlvPosClgLlmt | Changeover Valve Position Cooling Low Limit | AV
ChgVlvPosHtgLlmt | Changeover Valve Position Heating Low Limit | AV
ChIsoVlvEsw | Chiller Isolation Valve End Switch | DI
ChIsoVlvEsw | Chiller Isolation Valve End Switch | DV
ChIsoVlvEswCls | Chiller Isolation Valve End Switch Close | DI
ChIsoVlvEswCls | Chiller Isolation Valve End Switch Close | DV
ChIsoVlvEswOpn | Chiller Isolation Valve End Switch Open | DI
ChIsoVlvEswOpn | Chiller Isolation Valve End Switch Open | DV
ChKw | Chiller Kilowatts | AI
ChKw | Chiller Kilowatts | AV
ChKwh | Chiller Kilowatt-Hours | AV
ChKwTot | Chiller Kilowatts Total | AV
ChLclLoc | Chiller Local Lockout | DV
ChLclLocRst | Chiller Local Lockout Reset | DV
ChLd | Chiller Lead Unit | AV
ChLdMan | Chiller Lead Unit Manual | AV
ChLdRotTs | Chiller Lead Rotation Schedule | AV
ChLg | Chiller Lag | AV
ChLgDof | Chiller Lag Delay Off | AV
ChLgDon | Chiller Lag Delay On | AV
ChLgMan | Chiller Lag Manual | AV
ChLiftMax | Chiller Maximum Lift | AV
ChLiftMin | Chiller Minimum Lift | AV
ChLoadAmp | Chiller Load Amps | AI
ChLoadAmp | Chiller Load Amps | AV
ChLoadAmpLmt | Chiller Load Amps Limit | AO
ChLoadAmpLmt | Chiller Load Amps Limit | AV
ChLoc | Chiller Lockout | DV
ChMaintMd | Chiller Maintenance Mode | DV
ChMaintMdAlm | Chiller Maintenance Mode Alarm | DV
ChMaintReqAlm | Chiller Maintenance Request Alarm | DV
ChMaintReqRtRst | Chiller Maintenance Request Run Time Reset | DV
ChMd | Chiller Mode | MV
ChNumAvl | Number of Chillers Available | AV
ChNumChwIsoVlvOpn | Number of Chillers with Open Chilled Water Valves | AV
ChNumCwIsoVlvOpn | Number of Chillers with Open Condenser Water Valves | AV
ChNumLclLoc | Number of Chillers In Local Lockout | AV
ChNumOvrOn | Number of Chillers Which Are Overridden On | AV
ChNumReq | Number of Chillers Request | AV
ChNumRun | Number of Chillers Running | AV
ChOaTmpEnaSpt | Chiller Outside Air Temperature Enable Setpoint | AV
ChOilDifPr | Chiller Oil Differential Pressure | AI
ChOilDifPr | Chiller Oil Differential Pressure | AV
ChOilPr | Chiller Oil Pressure | AI
ChOilPr | Chiller Oil Pressure | AV
ChOilTmp | Chiller Oil Temperature | AI
ChOilTmp | Chiller Oil Temperature | AV
ChOilTmpSpt | Chiller Oil Temperature Setpoint | AV
ChOvrOn | Chiller Overridden On | DV
ChPAmp | Chiller Pump Amps | AI
ChPAmp | Chiller Pump Amps | AV
ChPCmd | Chiller Pump Command | DO
ChPCmd | Chiller Pump Command | DV
ChPKw | Chiller Pump Kilowatts | AV
ChPKwh | Chiller Pump Kilowatt-Hours | AV
ChPKwTot | Chiller Pump Kilowatts Total | AV
ChPlf | Chiller Part Load Fraction | AI
ChPlf | Chiller Part Load Fraction | AV
ChPSpd | Chiller Pump Speed | AO
ChPSpd | Chiller Pump Speed | AV
ChPSts | Chiller Pump Status | DI
ChPSts | Chiller Pump Status | DV
ChRla | Chiller Run Load Amps | AV
ChRotCmdTs | Chiller Rotation Command From Time Schedule | DV
ChRotLdMan | Chiller Manual Lead Rotation | DV
ChRotLdMd | Chiller Lead Rotation Mode | MV
ChRotOrdManValid | Chiller Manual Rotation Order Valid | DV
ChRotOrdValid | Chiller Rotation Order Valid | DV
ChRotSel | Chiller Rotation Mode Selection | MV
ChRotSelfCor | Chiller Rotation Self Correcting Option | DV
ChRotSw | Chiller Rotation Switch | DV
ChRotTsFrcRot | Chiller Rotation Time Schedule Force Rotation Option | DV
ChRt | Chiller Run Time | AV
ChRTmp | Chiller Return Temperature | AI
ChRTmp | Chiller Return Temperature | AV
ChRtRst | Chiller Run Time Reset | DV
ChStgSpt | Chiller Staging Setpoint | AV
ChSTmp | Chiller Supply Temperature | AI
ChSTmp | Chiller Supply Temperature | AV
ChSts | Chiller Status | DI
ChSts | Chiller Status | DV
ChStsOvrAlm | Chiller Status Forced By Operator Alarm | DV
ChTh | Chiller Tons-Hour | AV
ChTmpAlm | Chiller Temperature Alarm | DV
ChTmpAlmSv | Chiller Temperature Alarm Shunt Variable | DV
ChwApprSpt | Chilled Water Approach Setpoint | AV
ChwBypFl | Chilled Water Bypass Flow | AI
ChwBypFl | Chilled Water Bypass Flow | AV
ChwBypFlDir | Chilled Water Bypass Flow Direction | DV
ChwBypTmp | Chilled Water Bypass Temperature | AI
ChwBypTmp | Chilled Water Bypass Temperature | AV
ChwBypVlvFalm | Chilled Water Bypass Valve Fail Alarm | DV
ChwBypVlvFbk | Chilled Water Bypass Valve Feedback | AI
ChwBypVlvFbk | Chilled Water Bypass Valve Feedback | AV
ChwBypVlvOvrAlm | Chilled Water Bypass Valve Forced By Operator Alarm | DV
ChwBypVlvPos | Chilled Water Bypass Valve Position | AO
ChwBypVlvPos | Chilled Water Bypass Valve Position | AV
ChwCostRate | Chilled Water Cost Rate | AV
ChwDcpFl | Chilled Water Decoupler Flow | AI
ChwDcpFl | Chilled Water Decoupler Flow | AV
ChwDcpTmp | Chilled Water Decoupler Temperature | AI
ChwDcpTmp | Chilled Water Decoupler Temperature | AV
ChwDifPr | Chilled Water Differential Pressure | AI
ChwDifPr | Chilled Water Differential Pressure | AV
ChwDifPrAlm | Chilled Water Differential Pressure Alarm | DV
ChwDifPrCalAlm | Chilled Water Differential Pressure Calibration Alarm | DV
ChwDifPrDz | Chilled Water Differential Pressure Dead Zone | AV
ChwDifPrErrThr | Chilled Water Differential Pressure Error Threshold | AV
ChwDifPrHiErr | Chilled Water Differential Pressure High Error | AV
ChwDifPrHiErrStep | Chilled Water Differential Pressure High Error Step Size | AV
ChwDifPrLoErrStep | Chilled Water Differential Pressure Low Error Step Size | AV
ChwDifPrRate | Chilled Water Differential Pressure Sample Rate | AV
ChwDifPrSpt | Chilled Water Differential Pressure Setpoint | AV
ChwDifPrSptMax | Chilled Water Differential Pressure Maximum Setpoint | AV
ChwDifPrSptMin | Chilled Water Differential Pressure Minimum Setpoint | AV
ChwDifPrSptRstDlyDn | Chilled Water Differential Pressure Setpoint Reset Delay Down | AV
ChwDifPrSptRstDlyUp | Chilled Water Differential Pressure Setpoint Reset Delay Up | AV
ChwDifPrSptRstHi | Chilled Water Differential Pressure Setpoint Reset High | AV
ChwDifPrSptRstLo | Chilled Water Differential Pressure Setpoint Reset Low | AV
ChwDifTmp | Chilled Water Differential Temperature | AV
ChwFl | Chilled Water Flow | AI
ChwFl | Chilled Water Flow | AV
ChwFlDir | Chilled Water Flow Direction | DV
ChwFlErrThr | Chilled Water Flow Error Threshold | AV
ChwFlFalm | Chilled Water Flow Fail Alarm | DV
ChwFlHalm | Chilled Water Flow High Alarm | DV
ChwFlLalm | Chilled Water Flow Low Alarm | DV
ChwFlLo | Minimum Chilled Water Flow | AV
ChwFlLoSpt | Minimum Chilled Water Flow Setpoint | AV
ChwFlSpt | Chilled Water Flow Setpoint | AV
ChwHxNumRun | Number of Chilled Water Heat Exchangers Running | AV
ChwMixVlvPos | Chilled Water Mixing Valve Position | AO
ChwMixVlvPos | Chilled Water Mixing Valve Position | AV
ChwPAlm | Chilled Water Pump Alarm | DI
ChwPAlm | Chilled Water Pump Alarm | DV
ChwPAmp | Chilled Water Pump Amps | AI
ChwPAmp | Chilled Water Pump Amps | AV
ChwPCmd | Chilled Water Pump Command | DO
ChwPCmd | Chilled Water Pump Command | DV
ChwPDifPr | Chilled Water Pump Differential Pressure | AI
ChwPDifPr | Chilled Water Pump Differential Pressure | AV
ChwPFbk | Chilled Water Pump Feedback | AI
ChwPFbk | Chilled Water Pump Feedback | AV
ChwPLd | Chilled Water Pump Lead | AV
ChwPLg | Chilled Water Pump Lag | AV
ChwPRt | Chilled Water Pump Run Time | AV
ChwPrVlvPos | Chilled Water Pressure Valve Position | AO
ChwPrVlvPos | Chilled Water Pressure Valve Position | AV
ChwPSpd | Chilled Water Pump Speed | AO
ChwPSpd | Chilled Water Pump Speed | AV
ChwPSts | Chilled Water Pump Status | DI
ChwPSts | Chilled Water Pump Status | DV
ChwReqPct | Chilled Water Request Hours as Percent | AV
ChwReqRst | Chilled Water Request Hours Reset | DV
ChwReqRt | Chilled Water Request Hours | AV
ChwRFl | Chilled Water Return Flow | AI
ChwRFl | Chilled Water Return Flow | AV
ChwRPr | Chilled Water Return Pressure | AI
ChwRPr | Chilled Water Return Pressure | AV
ChwRstReq | Chilled Water Reset Requests | AV
ChwRTmp | Chilled Water Return Temperature | AI
ChwRTmp | Chilled Water Return Temperature | AV
ChwRTmpFalm | Chilled Water Return Temperature Fail Alarm | DV
ChwRTmpHalm | Chilled Water Return Temperature High Alarm | DV
ChwRTmpLalm | Chilled Water Return Temperature Low Alarm | DV
ChwRTmpSpt | Chilled Water Return Temperature Setpoint | AV
ChwSFl | Chilled Water Supply Flow | AI
ChwSFl | Chilled Water Supply Flow | AV
ChwSFlAlm | Chilled Water Supply Flow Alarm | DV
ChwSFlCalAlm | Chilled Water Supply Flow Calibration Alarm | DV
ChwSFlSptMin | Chilled Water Supply Flow Minimum Setpoint | AV
ChwSPr | Chilled Water Supply Pressure | AI
ChwSPr | Chilled Water Supply Pressure | AV
ChwSPrSpt | Chilled Water Supply Pressure Setpoint | AV
ChwSTmp | Chilled Water Supply Temperature | AI
ChwSTmp | Chilled Water Supply Temperature | AV
ChwSTmpAlm | Chilled Water Supply Temperature Alarm | DV
ChwSTmpAlmSv | Chilled Water Supply Temperature Alarm Shunt Variable | DV
ChwSTmpFalm | Chilled Water Supply Temperature Fail Alarm | DV
ChwSTmpHalm | Chilled Water Supply Temperature High Alarm | DV
ChwSTmpLalm | Chilled Water Supply Temperature Low Alarm | DV
ChwSTmpSpt | Chilled Water Supply Temperature Setpoint | AV
ChwSTmpSptMax | Chilled Water Supply Temperature Maximum Setpoint | AV
ChwSTmpSptMin | Chilled Water Supply Temperature Minimum Setpoint | AV
ChwSTmpSptRstDlyDn | Chilled Water Supply Temperature Setpoint Reset Delay Down | AV
ChwSTmpSptRstDlyUp | Chilled Water Supply Temperature Setpoint Reset Delay Up | AV
ChwSTmpSptRstHi | Chilled Water Supply Temperature Setpoint Reset High | AV
ChwSTmpSptRstLo | Chilled Water Supply Temperature Setpoint Reset Low | AV
ChwSTmpSptTestMdAlm | Chilled Water Supply Temperature Setpoint Reset Test Mode Alarm | DV
ChwSVlvPos | Chilled Water Supply Valve Position | AO
ChwSVlvPos | Chilled Water Supply Valve Position | AV
ChwSysAlmInh | Chilled Water System Alarm Inhibit | DV
ChwSysAvl | Chilled Water System Available | DV
ChwSysEna | Chilled Water System Enable | DV
ChwSysKwTot | Chilled Water System Kilowatts Total | AV
ChwSysPlf | Chilled Water System Part Load Fraction | AV
ChwSysReq | Chilled Water System Request To Run | DV
ChwSysReqCnt | Chilled Water System Request Count | AV
ChwSysReqIgnCnt | Chilled Water System Ignored Request Count | AV
ChwSysReqPct | Chilled Water System Request Hours as Percent | AV
ChwSysReqRst | Chilled Water System Request Hours Reset | DV
ChwSysReqRt | Chilled Water System Request Hours | AV
ChwSysRst | Chilled Water System Master Alarm Reset | DV
ChwSysRstPct | Chilled Water System Setpoint Reset Percent | AV
ChwSysRstReqCnt | Chilled Water System Reset Request Count | AV
ChwSysRstReqIgnCnt | Chilled Water System Ignored Requests Count | AV
ChwSysSts | Chilled Water System Status | DV
ChwTmpDlt | Chilled Water Delta Temperature | AV
ChwTmpErrThr | Chilled Water Temperature Error Threshold | AV
ChwVlvCmd | Chilled Water Valve Command | DO
ChwVlvCmd | Chilled Water Valve Command | DV
ChwVlvCmdCls | Chilled Water Valve Close Command | DO
ChwVlvCmdCls | Chilled Water Valve Close Command | DV
ChwVlvCmdOpn | Chilled Water Valve Open Command | DO
ChwVlvCmdOpn | Chilled Water Valve Open Command | DV
ChwVlvFbk | Chilled Water Valve Feedback | AI
ChwVlvFbk | Chilled Water Valve Feedback | AV
ChwVlvLoad | Chilled Water Valve Load | AV
ChwVlvMaxOpnDz | Most Open Chilled Water Valve Dead Zone | AV
ChwVlvMaxOpnSpt | Most Open Chilled Water Valve Setpoint | AV
ChwVlvPos | Chilled Water Valve Position | AO
ChwVlvPos | Chilled Water Valve Position | AV
ChwVlvPosAvg | Average Chilled Water Valve Position | AV
ChwVlvPosHi | Highest Chilled Water Valve Position | AV
ChwVlvPosLo | Lowest Chilled Water Valve Position | AV
ChXrt | Chiller Extended Run Time | AV
ClgBypDprPos | Cooling Bypass Damper Position | AO
ClgBypDprPos | Cooling Bypass Damper Position | AV
ClgCap | Cooling Capacity | AV
ClgCmd | Cooling Command | DO
ClgCmd | Cooling Command | DV
ClgCph | Cooling Cycles per Hour | AV
ClgDchrgTmpAvg | Cooling Discharge Air Temperature Average | AV
ClgDmnd | Cooling Demand | AV
ClgEf | Cooling Efficiency | AV
ClgEntTmpAvg | Cooling Entering Air Temperature Average | AV
ClgLoad | Cooling Load | AV
ClgMd | Cooling Mode | MV
ClgOaTmpLocSpt | Cooling Operation Outside Air Temperature Lockout Setpoint | AV
ClgPCmd | Cooling Pump Command | DO
ClgPCmd | Cooling Pump Command | DV
ClgPSts | Cooling Pump Status | DI
ClgPSts | Cooling Pump Status | DV
ClgRstReq | Cooling Reset Request | AV
ClgRstReqHalm | Cooling Reset Request High Alarm | DV
ClgRstReqHalmSv | Cooling Reset Request High Alarm Shunt Variable | DV
ClgRstReqPct | Cooling Reset Request Hours as Percent | AV
ClgRstReqRst | Cooling Reset Request Hours Reset | DV
ClgRstReqRt | Cooling Reset Request Hours | AV
ClgRTmp | Cooling Return Water Temperature | AI
ClgRTmp | Cooling Return Water Temperature | AV
ClgSaRh | Cooling Supply Air Relative Humidity | AI
ClgSaRh | Cooling Supply Air Relative Humidity | AV
ClgSaTmp | Cooling Supply Air Temperature | AI
ClgSaTmp | Cooling Supply Air Temperature | AV
ClgSaTmpAvg | Cooling Supply Air Temperature Average | AV
ClgSaTmpSpt | Cooling Supply Air Temperature Setpoint | AV
ClgStgCmd | Cooling Stage Command | DO
ClgStgCmd | Cooling Stage Command | DV
ClgStgNum | Number of Cooling Stages | AV
ClgSTmp | Cooling Supply Water Temperature | AI
ClgSTmp | Cooling Supply Water Temperature | AV
ClgSts | Cooling Status | DI
ClgSts | Cooling Status | DV
ClgTestMd | Cooling Test Mode | MV
ClgTestSts | Cooling Test Status | MV
ClgTmp | Cooling Temperature | AI
ClgTmp | Cooling Temperature | AV
ClgTmpSpt | Cooling Temperature Setpoint | AV
ClgUvLtAlm | Cooling Ultraviolet Light Alarm | DI
ClgUvLtAlm | Cooling Ultraviolet Light Alarm | DV
ClgUvLtCmd | Cooling Ultraviolet Light Command | DO
ClgUvLtCmd | Cooling Ultraviolet Light Command | DV
ClgUvLtFlt | Cooling Ultraviolet Light Fault | DI
ClgUvLtFlt | Cooling Ultraviolet Light Fault | DV
ClgUvLtFof | Cooling Ultraviolet Light Fail Off Alarm | DV
ClgUvLtFon | Cooling Ultraviolet Light Fail On Alarm | DV
ClgUvLtRt | Cooling Ultraviolet Light Run Time | AV
ClgUvLtSts | Cooling Ultraviolet Light Status | DI
ClgUvLtSts | Cooling Ultraviolet Light Status | DV
ClgVlvFbk | Cooling Valve Feedback | AI
ClgVlvFbk | Cooling Valve Feedback | AV
ClgVlvPos | Cooling Valve Position | AO
ClgVlvPos | Cooling Valve Position | AV
ClgVlvPosMin | Cooling Valve Minimum Position | AV
ClrTmp | Cooler Temperature | AI
ClrTmp | Cooler Temperature | AV
ClsofTestSts | Close Off Test Status | MV
CmpAirSPr | Compressed Air Supply Pressure | AI
CmpAirSPr | Compressed Air Supply Pressure | AV
CmpAirTnkPr | Compressed Air Tank Pressure | AI
CmpAirTnkPr | Compressed Air Tank Pressure | AV
CmpAlm | Compressor Alarm | DI
CmpAlm | Compressor Alarm | DV
CmpAmp | Compressor Amps | AI
CmpAmp | Compressor Amps | AV
CmpCmd | Compressor Command | DO
CmpCmd | Compressor Command | DV
CmpElecKw | Compressor Electrical Kilowatts | AV
CmpElecKwh | Compressor Electrical Kilowatt-Hours | AV
CmpOaTmpLocSpt | Compressor Outside Air Temperature Lockout Setpoint | AV
CmpRfgKw | Compressor Refrigerant Kilowatts | AV
CmpRfgKwh | Compressor Refrigerant Kilowatt-Hours | AV
CmpRfgPrSpt | Compressor Refrigerant Pressure Setpoint | AV
CmpRfgRPr | Compressor Refrigerant Return Pressure | AI
CmpRfgRPr | Compressor Refrigerant Return Pressure | AV
CmpRfgRTmp | Compressor Refrigerant Return Temperature | AI
CmpRfgRTmp | Compressor Refrigerant Return Temperature | AV
CmpRfgSPr | Compressor Refrigerant Supply Pressure | AI
CmpRfgSPr | Compressor Refrigerant Supply Pressure | AV
CmpRfgSTmp | Compressor Refrigerant Supply Temperature | AI
CmpRfgSTmp | Compressor Refrigerant Supply Temperature | AV
CmpStgCmd | Compressor Stage Command | DO
CmpStgCmd | Compressor Stage Command | DV
CmpStgSts | Compressor Stage Status | DI
CmpStgSts | Compressor Stage Status | DV
CmpSts | Compressor Status | DI
CmpSts | Compressor Status | DV
CndAlm | Condensate Alarm | DI
CndAlm | Condensate Alarm | DV
CndLvlAlm | Condensate Level Alarm | DI
CndLvlAlm | Condensate Level Alarm | DV
CndPSts | Condensate Pump Status | DI
CndPSts | Condensate Pump Status | DV
CndRFl | Condensate Return Flow | AI
CndRFl | Condensate Return Flow | AV
CndRTmp | Condensate Return Temperature | AI
CndRTmp | Condensate Return Temperature | AV
CO2Max | Maximum Carbon Dioxide | AV
CO2Md | Carbon Dioxide Mode | MV
COAlm | Carbon Monoxide Alarm | DI
COAlm | Carbon Monoxide Alarm | DV
CogenRTmp | Cogeneration Return Temperature | AI
CogenRTmp | Cogeneration Return Temperature | AV
CogenSTmp | Cogeneration Supply Temperature | AI
CogenSTmp | Cogeneration Supply Temperature | AV
COMax | Maximum Carbon Monoxide | AV
CondAlm | Condenser Alarm | DI
CondAlm | Condenser Alarm | DV
CondBlrHwSTmp | Common Condensing Boiler Hot Water Supply Temperature | AI
CondBlrHwSTmp | Common Condensing Boiler Hot Water Supply Temperature | AV
CondBlrHwSTmpSptMax | Condensing Boiler Maximum Hot Water Supply Temperature Setpoint | AV
CondBypVlvPos | Condenser Bypass Valve Position | AO
CondBypVlvPos | Condenser Bypass Valve Position | AV
CondCmd | Condenser Command | DO
CondCmd | Condenser Command | DV
CondFanAmp | Condenser Fan Amps | AI
CondFanAmp | Condenser Fan Amps | AV
CondFanCmd | Condenser Fan Command | DO
CondFanCmd | Condenser Fan Command | DV
CondFanKw | Condenser Fan Kilowatts | AV
CondFanKwh | Condenser Fan Kilowatt-Hours | AV
CondFanSpd | Condenser Fan Speed | AI
CondFanSpd | Condenser Fan Speed | AV
CondFanSts | Condenser Fan Status | DI
CondFanSts | Condenser Fan Status | DV
CondIsoVlvPos | Condenser Isolation Valve Position | AO
CondIsoVlvPos | Condenser Isolation Valve Position | AV
CondPCmd | Condenser Pump Command | DO
CondPCmd | Condenser Pump Command | DV
CondPSts | Condenser Pump Status | DI
CondPSts | Condenser Pump Status | DV
CondRfgEnth | Condenser Refrigerant Enthalpy | AI
CondRfgEnth | Condenser Refrigerant Enthalpy | AV
CondRfgPr | Condenser Refrigerant Pressure | AI
CondRfgPr | Condenser Refrigerant Pressure | AV
CondRfgREnth | Condenser Refrigerant Return Enthalpy | AI
CondRfgREnth | Condenser Refrigerant Return Enthalpy | AV
CondRfgRTmp | Condenser Refrigerant Return Temperature | AI
CondRfgRTmp | Condenser Refrigerant Return Temperature | AV
CondRfgTmp | Condenser Refrigerant Temperature | AI
CondRfgTmp | Condenser Refrigerant Temperature | AV
CondRTmp | Condenser Return Temperature | AI
CondRTmp | Condenser Return Temperature | AV
CondSts | Condenser Status | DI
CondSts | Condenser Status | DV
ConvVlvCmd | Convector Valve Command | DO
ConvVlvCmd | Convector Valve Command | DV
ConvVlvPos | Convector Valve Position | AO
ConvVlvPos | Convector Valve Position | AV
CtAlm | Cooling Tower Alarm | DI
CtAlm | Cooling Tower Alarm | DV
CtBdMtrCnt | Cooling Tower Blow Down Water Meter Count | AI
CtBdMtrCnt | Cooling Tower Blow Down Water Meter Count | AV
CtBdMtrTot | Cooling Tower Blow Down Water Meter Total | AV
CtBdVlvCmd | Cooling Tower Blow Down Valve Command | DO
CtBdVlvCmd | Cooling Tower Blow Down Valve Command | DV
CtBsnHtgEna | Cooling Tower Basin Heating Enable | DV
CtBsnHtgFof | Cooling Tower Basin Heating Fail Off Alarm | DV
CtBsnHtgFon | Cooling Tower Basin Heating Fail On Alarm | DV
CtBsnHtgRt | Cooling Tower Basin Heating Run Time | AV
CtBsnHtgRtRst | Cooling Tower Basin Heating Run Time Reset | DV
CtBsnHtgSts | Cooling Tower Basin Heating Status | DI
CtBsnHtgSts | Cooling Tower Basin Heating Status | DV
CtBsnLvlAlmHiSpt | Cooling Tower Basin Level High Alarm Setpoint | AV
CtBsnLvlAlmLoSpt | Cooling Tower Basin Level Low Alarm Setpoint | AV
CtBsnSwpAlm | Cooling Tower Basin Sweeper Alarm | DI
CtBsnSwpAlm | Cooling Tower Basin Sweeper Alarm | DV
CtBsnSwpCmd | Cooling Tower Basin Sweeper Command | DO
CtBsnSwpCmd | Cooling Tower Basin Sweeper Command | DV
CtBsnSwpSts | Cooling Tower Basin Sweeper Status | DI
CtBsnSwpSts | Cooling Tower Basin Sweeper Status | DV
CtBsnTmp | Cooling Tower Basin Temperature | AI
CtBsnTmp | Cooling Tower Basin Temperature | AV
CtBsnTmpAlm | Cooling Tower Basin Temperature Alarm | DV
CtBsnTmpAlmLvl | Cooling Tower Basin Temperature Alarm Level | DV
CtBsnTmpAlmLvlSv | Cooling Tower Basin Temperature Alarm Shunt Variable | DV
CtBsnTmpSpt | Cooling Tower Basin Temperature Setpoint | AV
CtBsnTmpSptDif | Cooling Tower Basin Temperature Setpoint Differential | AV
CtBypVlvFbk | Cooling Tower Bypass Valve Feedback | AI
CtBypVlvFbk | Cooling Tower Bypass Valve Feedback | AV
CtBypVlvPos | Cooling Tower Bypass Valve Position | AO
CtBypVlvPos | Cooling Tower Bypass Valve Position | AV
CtCentSeprAlm | Cooling Tower Centrifugal Separator Alarm | DI
CtCentSeprAlm | Cooling Tower Centrifugal Separator Alarm | DV
CtCentSeprCmd | Cooling Tower Centrifugal Separator Command | DO
CtCentSeprCmd | Cooling Tower Centrifugal Separator Command | DV
CtCentSeprSts | Cooling Tower Centrifugal Separator Status | DI
CtCentSeprSts | Cooling Tower Centrifugal Separator Status | DV
CtCmd | Cooling Tower Command | DO
CtCmd | Cooling Tower Command | DV
CtCwRIsoVlvCmd | Cooling Tower Condenser Water Return Isolation Valve Command | DO
CtCwRIsoVlvCmd | Cooling Tower Condenser Water Return Isolation Valve Command | DV
CtCwRIsoVlvCmdCls | Cooling Tower Condenser Water Return Isolation Valve Close Command | DO
CtCwRIsoVlvCmdCls | Cooling Tower Condenser Water Return Isolation Valve Close Command | DV
CtCwRIsoVlvCmdOpn | Cooling Tower Condenser Water Return Isolation Valve Open Command | DO
CtCwRIsoVlvCmdOpn | Cooling Tower Condenser Water Return Isolation Valve Open Command | DV
CtCwRIsoVlvEsw | Cooling Tower Condenser Water Return Isolation Valve End Switch | DI
CtCwRIsoVlvEsw | Cooling Tower Condenser Water Return Isolation Valve End Switch | DV
CtCwRIsoVlvEswCls | Cooling Tower Condenser Water Return Isolation Valve End Switch Closed | DI
CtCwRIsoVlvEswCls | Cooling Tower Condenser Water Return Isolation Valve End Switch Closed | DV
CtCwRIsoVlvEswOpn | Cooling Tower Condenser Water Return Isolation Valve End Switch Open | DI
CtCwRIsoVlvEswOpn | Cooling Tower Condenser Water Return Isolation Valve End Switch Open | DV
CtCwRIsoVlvFbk | Cooling Tower Condenser Water Return Isolation Valve Feedback | AI
CtCwRIsoVlvFbk | Cooling Tower Condenser Water Return Isolation Valve Feedback | AV
CtCwRIsoVlvFcls | Cooling Tower Condenser Water Return Isolation Valve Fail Close Alarm | DV
CtCwRIsoVlvFopn | Cooling Tower Condenser Water Return Isolation Valve Fail Open Alarm | DV
CtCwSIsoVlvCmd | Cooling Tower Condenser Water Supply Isolation Valve Command | DO
CtCwSIsoVlvCmd | Cooling Tower Condenser Water Supply Isolation Valve Command | DV
CtCwSIsoVlvCmdCls | Cooling Tower Condenser Water Supply Isolation Valve Close Command | DO
CtCwSIsoVlvCmdCls | Cooling Tower Condenser Water Supply Isolation Valve Close Command | DV
CtCwSIsoVlvCmdOpn | Cooling Tower Condenser Water Supply Isolation Valve Open Command | DO
CtCwSIsoVlvCmdOpn | Cooling Tower Condenser Water Supply Isolation Valve Open Command | DV
CtCwSIsoVlvEsw | Cooling Tower Condenser Water Supply Isolation Valve End Switch | DI
CtCwSIsoVlvEsw | Cooling Tower Condenser Water Supply Isolation Valve End Switch | DV
CtCwSIsoVlvEswCls | Cooling Tower Condenser Water Supply Isolation Valve End Switch Closed | DI
CtCwSIsoVlvEswCls | Cooling Tower Condenser Water Supply Isolation Valve End Switch Closed | DV
CtCwSIsoVlvEswOpn | Cooling Tower Condenser Water Supply Isolation Valve End Switch Open | DI
CtCwSIsoVlvEswOpn | Cooling Tower Condenser Water Supply Isolation Valve End Switch Open | DV
CtCwSIsoVlvFbk | Cooling Tower Condenser Water Supply Isolation Valve Feedback | AI
CtCwSIsoVlvFbk | Cooling Tower Condenser Water Supply Isolation Valve Feedback | AV
CtCwSIsoVlvFcls | Cooling Tower Condenser Water Supply Isolation Valve Fail Close Alarm | DV
CtCwSIsoVlvFopn | Cooling Tower Condenser Water Supply Isolation Valve Fail Open Alarm | DV
CtEna | Cooling Tower Enable | DV
CtFanAlm | Cooling Tower Fan Alarm | DI
CtFanAlm | Cooling Tower Fan Alarm | DV
CtFanAmp | Cooling Tower Fan Amps | AI
CtFanAmp | Cooling Tower Fan Amps | AV
CtFanCmd | Cooling Tower Fan Command | DO
CtFanCmd | Cooling Tower Fan Command | DV
CtFanCmdDof | Cooling Tower Fan Command Delay Off | AV
CtFanCmdDon | Cooling Tower Fan Command Delay On | AV
CtFanCmdHi | Cooling Tower Fan High Speed Command | DO
CtFanCmdHi | Cooling Tower Fan High Speed Command | DV
CtFanCmdLo | Cooling Tower Fan Low Speed Command | DO
CtFanCmdLo | Cooling Tower Fan Low Speed Command | DV
CtFanCmdMed | Cooling Tower Fan Medium Speed Command | DO
CtFanCmdMed | Cooling Tower Fan Medium Speed Command | DV
CtFanCmdMinOff | Cooling Tower Command Minimum Off Time | AV
CtFanCmdOvrAlm | Cooling Tower Fan Command Forced By Operator Alarm | DV
CtFanEna | Cooling Tower Fan Enable | DV
CtFanEnaHi | Cooling Tower Fan High Enable | DV
CtFanEnaLo | Cooling Tower Fan Low Enable | DV
CtFanFbk | Cooling Tower Fan Feedback | AI
CtFanFbk | Cooling Tower Fan Feedback | AV
CtFanFof | Cooling Tower Fan Fail Off Alarm | DV
CtFanFon | Cooling Tower Fan Fail On Alarm | DV
CtFanFreq | Cooling Tower Fan Frequency | AO
CtFanFreq | Cooling Tower Fan Frequency | AV
CtFanFreqSpt | Cooling Tower Fan Frequency Setpoint | AV
CtFanKw | Cooling Tower Fan Kilowatts | AI
CtFanKw | Cooling Tower Fan Kilowatts | AV
CtFanKwh | Cooling Tower Fan Kilowatt-Hours | AV
CtFanKwMax | Cooling Tower Fan Kilowatt Maximum | AV
CtFanKwTot | Cooling Tower Fan Kilowatts Total | AI
CtFanKwTot | Cooling Tower Fan Kilowatts Total | AV
CtFanRt | Cooling Tower Fan Run Time | AV
CtFanRtRst | Cooling Tower Fan Run Time Reset | DV
CtFanSpd | Cooling Tower Fan Speed | AO
CtFanSpd | Cooling Tower Fan Speed | AV
CtFanSpdFbk | Cooling Tower Fan Speed Feedback | AI
CtFanSpdFbk | Cooling Tower Fan Speed Feedback | AV
CtFanSpdHlmt | Cooling Tower Fan Speed High Limit | AV
CtFanSpdLlmt | Cooling Tower Fan Speed Low Limit | AV
CtFanSpdMin | Cooling Tower Fan Minimum Speed | AV
CtFanSpdOvrAlm | Cooling Tower Fan Speed Forced By Operator Alarm | DV
CtFanSts | Cooling Tower Fan Status | DI
CtFanSts | Cooling Tower Fan Status | DV
CtFanStsHi | Cooling Tower Fan High Speed Status | DI
CtFanStsHi | Cooling Tower Fan High Speed Status | DV
CtFanStsLo | Cooling Tower Fan Low Speed Status | DI
CtFanStsLo | Cooling Tower Fan Low Speed Status | DV
CtFanStsMed | Cooling Tower Fan Medium Speed Status | DI
CtFanStsMed | Cooling Tower Fan Medium Speed Status | DV
CtFanStsOvrAlm | Cooling Tower Fan Status Forced By Operator Alarm | DV
CtFanVfdAlm | Cooling Tower Fan Variable Frequency Drive Alarm | DI
CtFanVfdAlm | Cooling Tower Fan Variable Frequency Drive Alarm | DV
CtFanVibSwSts | Cooling Tower Vibration Switch Status | DI
CtFanVibSwSts | Cooling Tower Vibration Switch Status | DV
CtFof | Cooling Tower Fail Off Alarm | DV
CtFon | Cooling Tower Fail On Alarm | DV
CtHtrcEna | Cooling Tower Heat Trace Enable | DO
CtHtrcEna | Cooling Tower Heat Trace Enable | DV
CtHtrcFof | Cooling Tower Heat Trace Fail Off Alarm | DV
CtHtrcFofSv | Cooling Tower Heat Trace Fail Off Alarm Shunt Variable | DV
CtHtrcFon | Cooling Tower Heat Trace Fail On Alarm | DV
CtHtrcFonSv | Cooling Tower Heat Trace Fail On Alarm Shunt Variable | DV
CtHtrcSts | Cooling Tower Heat Trace Status | DI
CtHtrcSts | Cooling Tower Heat Trace Status | DV
CtIsoVlvPos | Cooling Tower Isolation Valve Position | AO
CtIsoVlvPos | Cooling Tower Isolation Valve Position | AV
CtLclLoc | Cooling Tower Local Lockout | DV
CtLclLocRst | Cooling Tower Local Lockout Reset | DV
CtLd | Cooling Tower Lead | AV
CtLdMan | Cooling Tower Lead Man | AV
CtLg | Cooling Tower Lag Order | AV
CtLgMan | Cooling Tower Lag Order Manual | AV
CtMaintMd | Cooling Tower Maintenance Mode | DV
CtMaintMdAlm | Cooling Tower Maintenance Mode Alarm | DV
CtMaintReqAlm | Cooling Tower Maintenance Request Alarm | DV
CtMaintReqRtRst | Cooling Tower Maintenance Request Run Time Reset | DV
CtMuwMtrCnt | Cooling Tower Makeup Water Meter Count | AI
CtMuwMtrCnt | Cooling Tower Makeup Water Meter Count | AV
CtMuwMtrTot | Cooling Tower Makeup Water Meter Total | AV
CtNumAvl | Number of Cooling Towers Available | AV
CtNumLclLoc | Number of Cooling Towers In Local Lockout | AV
CtNumOvrOn | Number of Cooling Towers Which Are Overridden On | AV
CtNumReq | Number of Cooling Towers Requested | AV
CtNumRun | Number of Cooling Towers Running | AV
CtOvrOn | Cooling Tower Overridden On | DV
CtRotCmdTs | Cooling Tower Rotation Command From Time Schedule | DV
CtRotOrdManValid | Cooling Tower Manual Rotation Order Valid | DV
CtRotOrdValid | Cooling Tower Rotation Order Valid | DV
CtRotSel | Cooling Tower Rotation Mode Select | MV
CtRotSelfCor | Cooling Tower Rotation Self Correcting Option | DV
CtRotSw | Cooling Tower Rotation Switch | DV
CtRotTsFrcRot | Cooling Tower Rotation Time Schedule Force Rotation Option | DV
CtRt | Cooling Tower Run Time | AV
CtRTmp | Cooling Tower Return Temperature | AI
CtRTmp | Cooling Tower Return Temperature | AV
CtRtRst | Cooling Tower Run Time Reset | DV
CtSandFilAlm | Cooling Tower Sand Filter Alarm | DI
CtSandFilAlm | Cooling Tower Sand Filter Alarm | DV
CtSandFilDifPr | Cooling Tower Sand Filter Differential Pressure | AI
CtSandFilDifPr | Cooling Tower Sand Filter Differential Pressure | AV
CtSandFilSts | Cooling Tower Sand Filter Status | DI
CtSandFilSts | Cooling Tower Sand Filter Status | DV
CtSpyCmd | Cooling Tower Spray Command | DO
CtSpyCmd | Cooling Tower Spray Command | DV
CtSpyOaTmpLocSpt | Cooling Tower Spray Operation Outside Air Temperature Lockout Setpoint | AV
CtSpySts | Cooling Tower Spray Status | DI
CtSpySts | Cooling Tower Spray Status | DV
CtSTmp | Cooling Tower Supply Temperature | AI
CtSTmp | Cooling Tower Supply Temperature | AV
CtSts | Cooling Tower Status | DI
CtSts | Cooling Tower Status | DV
CtTmtSts | Cooling Tower Water Treatment Status | DI
CtTmtSts | Cooling Tower Water Treatment Status | DV
CtXrt | Cooling Tower Extended Run Time | AV
CwApprSpt | Condenser Water Approach Setpoint | AV
CwBypVlvFbk | Condenser Water Bypass Valve Feedback | AI
CwBypVlvFbk | Condenser Water Bypass Valve Feedback | AV
CwBypVlvPos | Condenser Water Bypass Valve Position | AO
CwBypVlvPos | Condenser Water Bypass Valve Position | AV
CwDifPr | Condenser Water Differential Pressure | AI
CwDifPr | Condenser Water Differential Pressure | AV
CwDifPrSpt | Condenser Water Differential Pressure Setpoint | AV
CwDifPrVlvPos | Condenser Water Differential Pressure Valve Position | AO
CwDifPrVlvPos | Condenser Water Differential Pressure Valve Position | AV
CwEna | Condenser Water Enable | DV
CwFl | Condenser Water Flow | AI
CwFl | Condenser Water Flow | AV
CwFlFalm | Condenser Water Flow Fail Alarm | DV
CwFlHalm | Condenser Water Flow High Alarm | DV
CwFlLalm | Condenser Water Flow Low Alarm | DV
CwFlSpt | Condenser Water Flow Setpoint | AV
CwFlSts | Condenser Water Flow Status | DI
CwFlSts | Condenser Water Flow Status | DV
CwHtgRate | Condenser Water Heating Rate | AV
CwHxChwDifPr | Condenser Water Heat Exchanger Chilled Water Differential Pressure | AI
CwHxChwDifPr | Condenser Water Heat Exchanger Chilled Water Differential Pressure | AV
CwHxChwFl | Condenser Water Heat Exchanger Chilled Water Flow | AI
CwHxChwFl | Condenser Water Heat Exchanger Chilled Water Flow | AV
CwHxChwRIsoVlvCmd | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Command | DO
CwHxChwRIsoVlvCmd | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Command | DV
CwHxChwRIsoVlvCmdCls | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Close Command | DO
CwHxChwRIsoVlvCmdCls | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Close Command | DV
CwHxChwRIsoVlvCmdOpn | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Open Command | DO
CwHxChwRIsoVlvCmdOpn | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Open Command | DV
CwHxChwRIsoVlvEsw | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve End Switch | DI
CwHxChwRIsoVlvEsw | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve End Switch | DV
CwHxChwRIsoVlvEswCls | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve End Switch Closed | DI
CwHxChwRIsoVlvEswCls | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve End Switch Closed | DV
CwHxChwRIsoVlvEswOpn | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve End Switch Open | DI
CwHxChwRIsoVlvEswOpn | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve End Switch Open | DV
CwHxChwRIsoVlvFcls | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Fail Close Alarm | DV
CwHxChwRIsoVlvFopn | Condenser Water Heat Exchanger Chilled Water Return Isolation Valve Fail Open Alarm | DV
CwHxChwRTmp | Condenser Water Heat Exchanger Chilled Water Return Temperature | AI
CwHxChwRTmp | Condenser Water Heat Exchanger Chilled Water Return Temperature | AV
CwHxChwSIsoVlvCmd | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Command | DO
CwHxChwSIsoVlvCmd | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Command | DV
CwHxChwSIsoVlvCmdCls | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Close Command | DO
CwHxChwSIsoVlvCmdCls | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Close Command | DV
CwHxChwSIsoVlvCmdOpn | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Open Command | DO
CwHxChwSIsoVlvCmdOpn | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Open Command | DV
CwHxChwSIsoVlvEsw | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve End Switch | DI
CwHxChwSIsoVlvEsw | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve End Switch | DV
CwHxChwSIsoVlvEswCls | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve End Switch Closed | DI
CwHxChwSIsoVlvEswCls | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve End Switch Closed | DV
CwHxChwSIsoVlvEswOpn | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve End Switch Open | DI
CwHxChwSIsoVlvEswOpn | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve End Switch Open | DV
CwHxChwSIsoVlvFcls | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Fail Close Alarm | DV
CwHxChwSIsoVlvFopn | Condenser Water Heat Exchanger Chilled Water Supply Isolation Valve Fail Open Alarm | DV
CwHxChwSTmp | Condenser Water Heat Exchanger Chilled Water Supply Temperature | AI
CwHxChwSTmp | Condenser Water Heat Exchanger Chilled Water Supply Temperature | AV
CwHxCwDifPr | Condenser Water Heat Exchanger Condenser Water Differential Pressure | AI
CwHxCwDifPr | Condenser Water Heat Exchanger Condenser Water Differential Pressure | AV
CwHxCwFl | Condenser Water Heat Exchanger Condenser Water Flow | AI
CwHxCwFl | Condenser Water Heat Exchanger Condenser Water Flow | AV
CwHxCwRIsoVlvCmd | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Command | DO
CwHxCwRIsoVlvCmd | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Command | DV
CwHxCwRIsoVlvCmdCls | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Close Command | DO
CwHxCwRIsoVlvCmdCls | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Close Command | DV
CwHxCwRIsoVlvCmdOpn | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Open Command | DO
CwHxCwRIsoVlvCmdOpn | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Open Command | DV
CwHxCwRIsoVlvEsw | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve End Switch | DI
CwHxCwRIsoVlvEsw | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve End Switch | DV
CwHxCwRIsoVlvEswCls | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve End Switch Closed | DI
CwHxCwRIsoVlvEswCls | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve End Switch Closed | DV
CwHxCwRIsoVlvEswOpn | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve End Switch Open | DI
CwHxCwRIsoVlvEswOpn | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve End Switch Open | DV
CwHxCwRIsoVlvFcls | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Fail Close Alarm | DV
CwHxCwRIsoVlvFopn | Condenser Water Heat Exchanger Condenser Water Return Isolation Valve Fail Open Alarm | DV
CwHxCwRTmp | Condenser Water Heat Exchanger Condenser Water Return Temperature | AI
CwHxCwRTmp | Condenser Water Heat Exchanger Condenser Water Return Temperature | AV
CwHxCwSIsoVlvCmd | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Command | DO
CwHxCwSIsoVlvCmd | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Command | DV
CwHxCwSIsoVlvCmdCls | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Close Command | DO
CwHxCwSIsoVlvCmdCls | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Close Command | DV
CwHxCwSIsoVlvCmdOpn | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Open Command | DO
CwHxCwSIsoVlvCmdOpn | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Open Command | DV
CwHxCwSIsoVlvEsw | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve End Switch | DI
CwHxCwSIsoVlvEsw | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve End Switch | DV
CwHxCwSIsoVlvEswCls | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve End Switch Closed | DI
CwHxCwSIsoVlvEswCls | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve End Switch Closed | DV
CwHxCwSIsoVlvEswOpn | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve End Switch Open | DI
CwHxCwSIsoVlvEswOpn | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve End Switch Open | DV
CwHxCwSIsoVlvFcls | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Fail Close Alarm | DV
CwHxCwSIsoVlvFopn | Condenser Water Heat Exchanger Condenser Water Supply Isolation Valve Fail Open Alarm | DV
CwHxCwSTmp | Condenser Water Heat Exchanger Condenser Water Supply Temperature | AI
CwHxCwSTmp | Condenser Water Heat Exchanger Condenser Water Supply Temperature | AV
CwHxEna | Condenser Water Heat Exchanger Enable | DO
CwHxEna | Condenser Water Heat Exchanger Enable | DV
CwHxLclLoc | Condenser Water Heat Exchanger Local Lockout | DV
CwHxLd | Condenser Water Heat Exchanger Lead Unit | AV
CwHxLdMan | Condenser Water Heat Exchanger Lead Manual | AV
CwHxLg | Condenser Water Heat Exchanger Lag Unit | AV
CwHxLgMan | Condenser Water Heat Exchanger Lag Manual | AV
CwHxMaintMd | Condenser Water Heat Exchanger Maintenance Mode | DV
CwHxMaintMdAlm | Condenser Water Heat Exchanger Maintenance Mode Alarm | DV
CwHxMaintReqAlm | Condenser Water Heat Exchanger Maintenance Request Alarm | DV
CwHxMaintReqRtRst | Condenser Water Heat Exchanger Maintenance Request Run Time Reset | DV
CwHxOvrOn | Condenser Water Heat Exchanger Override On | DV
CwHxRotSel | Condenser Water Heat Exchanger Rotation Select | MV
CwHxRotSelfCor | Condenser Water Heat Exchanger Rotation Self Correcting Option | DV
CwHxRotTsFrcRot | Condenser Water Heat Exchanger Rotation Time Schedule Force Rotation Option | DV
CwHxRt | Condenser Water Heat Exchanger Run Time | AV
CwHxXrt | Condenser Water Heat Exchanger Extended Run Time | AV
CwPAmp | Condenser Water Pump Amps | AI
CwPAmp | Condenser Water Pump Amps | AV
CwPCmd | Condenser Water Pump Command | DO
CwPCmd | Condenser Water Pump Command | DV
CwPCmdDof | Condenser Water Pump Command Delay Off | AV
CwPCmdDon | Condenser Water Pump Command Delay On | AV
CwPCmdOvrAlm | Condenser Water Pump Command Forced By Operator Alarm | DV
CwPDifPr | Condenser Water Pump Differential Pressure | AI
CwPDifPr | Condenser Water Pump Differential Pressure | AV
CwPEna | Condenser Water Pump Enable | DV
CwPFbk | Condenser Water Pump Feedback | AI
CwPFbk | Condenser Water Pump Feedback | AV
CwPFl | Condenser Water Pump Flow | AI
CwPFl | Condenser Water Pump Flow | AV
CwPFof | Condenser Water Pump Fail Off Alarm | DV
CwPFon | Condenser Water Pump Fail On Alarm | DV
CwPFreq | Condenser Water Pump Frequency | AO
CwPFreq | Condenser Water Pump Frequency | AV
CwPKw | Condenser Water Pump Kilowatts | AI
CwPKw | Condenser Water Pump Kilowatts | AV
CwPKwh | Condenser Water Pump Kilowatt-Hours | AV
CwPKwMax | Condenser Water Pump Kilowatt Maximum | AV
CwPKwTot | Condenser Water Pump Kilowatts Total | AI
CwPKwTot | Condenser Water Pump Kilowatts Total | AV
CwPLclLoc | Condenser Water Pump Local Lockout | DV
CwPLclLocRst | Condenser Water Pump Local Lockout Reset | DV
CwPLd | Condenser Water Pump Lead | AV
CwPLdMan | Condenser Water Pump Lead Manual | AV
CwPLg | Condenser Water Pump Lag Order | AV
CwPLgMan | Condenser Water Pump Lag Order Manual | AV
CwPMaintMd | Condenser Water Pump Maintenance Mode | DV
CwPMaintMdAlm | Condenser Water Pump Maintenance Mode Alarm | DV
CwPMaintReqAlm | Condenser Water Pump Maintenance Request Alarm | DV
CwPMaintReqRtRst | Condenser Water Pump Maintenance Request Run Time Reset | DV
CwPNumAvl | Number of Condenser Water Pumps Available | AV
CwPNumLclLoc | Number of Condenser Water Pumps In Local Lockout | AV
CwPNumOvrOn | Number of Condenser Water Pumps Which Are Overridden On | AV
CwPNumReq | Number of Condenser Water Pumps Request | AV
CwPNumRun | Number of Condenser Water Pumps Running | AV
CwPOvrOn | Condenser Water Pump Overridden On | DV
CwPRotCmdTs | Condenser Water Pump Rotation Command From Time Schedule | DV
CwPRotOrdManValid | Condenser Water Pump Manual Rotation Order Valid | DV
CwPRotOrdValid | Condenser Water Pump Rotation Order Valid | DV
CwPRotSel | Condenser Water Pump Rotation Mode Select | MV
CwPRotSelfCor | Condenser Water Pump Rotation Self Correcting Option | DV
CwPRotSw | Condenser Water Pump Rotation Switch | DV
CwPRotTsFrcRot | Condenser Water Pump Rotation Time Schedule Force Rotation Option | DV
CwPRt | Condenser Water Pump Run Time | AV
CwPRtRst | Condenser Water Pump Run Time Reset | DV
CwPSpd | Condenser Water Pump Speed | AO
CwPSpd | Condenser Water Pump Speed | AV
CwPSpdFbk | Condenser Water Pump Speed Feedback | AI
CwPSpdFbk | Condenser Water Pump Speed Feedback | AV
CwPSpdHlmt | Condenser Water Pump Speed High Limit | AV
CwPSpdLlmt | Condenser Water Pump Speed Low Limit | AV
CwPSpdOvrAlm | Condenser Water Pump Speed Forced By Operator Alarm | DV
CwPSts | Condenser Water Pump Status | DI
CwPSts | Condenser Water Pump Status | DV
CwPStsOvrAlm | Condenser Water Pump Status Forced By Operator Alarm | DV
CwPVfdAlm | Condenser Water Pump Variable Frequency Drive Alarm | DI
CwPVfdAlm | Condenser Water Pump Variable Frequency Drive Alarm | DV
CwPXrt | Condenser Water Pump Extended Run Time | AV
CwRFl | Condenser Water Return Flow | AI
CwRFl | Condenser Water Return Flow | AV
CwRPr | Condenser Water Return Pressure | AI
CwRPr | Condenser Water Return Pressure | AV
CwRPrSpt | Condenser Water Return Pressure Setpoint | AV
CwRTmp | Condenser Water Return Temperature | AI
CwRTmp | Condenser Water Return Temperature | AV
CwRTmpFalm | Condenser Water Return Temperature Fail Alarm | DV
CwRTmpHalm | Condenser Water Return Temperature High Alarm | DV
CwRTmpLalm | Condenser Water Return Temperature Low Alarm | DV
CwRTmpSpt | Condenser Water Return Temperature Setpoint | AV
CwSFl | Condenser Water Supply Flow | AI
CwSFl | Condenser Water Supply Flow | AV
CwSPr | Condenser Water Supply Pressure | AI
CwSPr | Condenser Water Supply Pressure | AV
CwSTmp | Condenser Water Supply Temperature | AI
CwSTmp | Condenser Water Supply Temperature | AV
CwSTmpAlm | Condenser Water Supply Temperature Alarm | DV
CwSTmpAlmSv | Condenser Water Supply Temperature Alarm Shunt Variable | DV
CwSTmpDbd | Condenser Water Supply Temperature Deadband | AI
CwSTmpDbd | Condenser Water Supply Temperature Deadband | AV
CwSTmpDz | Condenser Water Supply Temperature Dead Zone | AV
CwSTmpFalm | Condenser Water Supply Temperature Fail Alarm | DV
CwSTmpHalm | Condenser Water Supply Temperature High Alarm | DV
CwSTmpLalm | Condenser Water Supply Temperature Low Alarm | DV
CwSTmpOfs | Condenser Water Supply Temperature Offset | AV
CwSTmpRstSptHi | Condenser Water Supply Temperature Setpoint Reset High | AV
CwSTmpRstSptLo | Condenser Water Supply Temperature Setpoint Reset Lo | AV
CwSTmpSpt | Condenser Water Supply Temperature Setpoint | AV
CwTh | Condenser Water Tons-Hour | AV
DebugAlm | Debug Alarm | DV
DebugAlmChw | Debug Alarm for Chilled Water System | DV
DebugAlmCw | Debug Alarm for Condenser Water System | DV
DebugAlmHw | Debug Alarm for Hot Water System | DV
DebugChw | Enable Alarm Debugging for Chilled Water System | DV
DebugCw | Enable Alarm Debugging for Condenser Water System | DV
DebugHw | Enable Alarm Debugging for Hot Water System | DV
DehCmd | Dehumidifier Command | DO
DehCmd | Dehumidifier Command | DV
DehDmnd | Dehumidifier Demand | AV
DehEna | Dehumidifier Enable | DV
DehEnaDif | Dehumidification Mode Enable Differential | AV
DehEnaSpt | Dehumidification Mode Enable Setpoint | AV
DehLoad | Dehumidification Load | AV
DehMd | Dehumidifier Mode | DV
DehMdChwVlvHlmt | Dehumidification Mode Chilled Water Valve High Limit | AV
DehMdEna | Dehumidifier Mode Enable | DV
DehOaTmpLocSpt | Dehumidifier Outside Air Temperature Lockout Setpoint | AV
DehPos | Dehumidifier Position | AV
DehSts | Dehumidifier Status | DI
DehSts | Dehumidifier Status | DV
DehTestMd | Dehumidification Test Mode | MV
DhwDifPr | Domestic Hot Water Differential Pressure | AI
DhwDifPr | Domestic Hot Water Differential Pressure | AV
DhwEna | Domestic Hot Water Enable | DO
DhwEna | Domestic Hot Water Enable | DV
DhwFl | Domestic Hot Water Flow | AI
DhwFl | Domestic Hot Water Flow | AV
DhwFlFalm | Domestic Hot Water Flow Fail Alarm | DV
DhwFlHalm | Domestic Hot Water Flow High Alarm | DV
DhwFlLalm | Domestic Hot Water Flow Low Alarm | DV
DhwHtgRate | Domestic Hot Water Heating Rate | AV
DhwPAmp | Domestic Hot Water Pump Amps | AI
DhwPAmp | Domestic Hot Water Pump Amps | AV
DhwPCmd | Domestic Hot Water Pump Command | DO
DhwPCmd | Domestic Hot Water Pump Command | DV
DhwPFl | Domestic Hot Water Pump Flow | AI
DhwPFl | Domestic Hot Water Pump Flow | AV
DhwPFreq | Domestic Hot Water Pump Frequency | AO
DhwPFreq | Domestic Hot Water Pump Frequency | AV
DhwPKw | Domestic Hot Water Kilowatts | AV
DhwPKwh | Domestic Hot Water Kilowatt-Hours | AV
DhwPSpd | Domestic Hot Water Pump Speed | AO
DhwPSpd | Domestic Hot Water Pump Speed | AV
DhwPSpdFbk | Domestic Hot Water Pump Speed Feedback | AI
DhwPSpdFbk | Domestic Hot Water Pump Speed Feedback | AV
DhwPSts | Domestic Hot Water Pump Status | DI
DhwPSts | Domestic Hot Water Pump Status | DV
DhwRcirSTmp | Domestic Hot Water Recirculation Supply Temperature | AI
DhwRcirSTmp | Domestic Hot Water Recirculation Supply Temperature | AV
DhwRTmp | Domestic Hot Water Return Temperature | AI
DhwRTmp | Domestic Hot Water Return Temperature | AV
DhwSTmp | Domestic Hot Water Supply Temperature | AI
DhwSTmp | Domestic Hot Water Supply Temperature | AV
DhwSTmpSpt | Domestic Hot Water Supply Temperature Setpoint | AV
DhwTnkHdrTmp | Domestic Hot Water Header Temperature | AI
DhwTnkHdrTmp | Domestic Hot Water Header Temperature | AV
DhwTnkHdrTmpSpt | Domestic Hot Water Tank Header Temperature Setpoint | AV
DhwTnkIsoVlvPos | Domestic Hot Water Isolation Valve Position | AO
DhwTnkIsoVlvPos | Domestic Hot Water Isolation Valve Position | AV
DhwTnkRTmp | Domestic Hot Water Tank Return Temperature | AI
DhwTnkRTmp | Domestic Hot Water Tank Return Temperature | AV
DhwTnkSTmp | Domestic Hot Water Tank Supply Temperature | AI
DhwTnkSTmp | Domestic Hot Water Tank Supply Temperature | AV
DhwTnkTmp | Domestic Hot Water Tank Temperature | AI
DhwTnkTmp | Domestic Hot Water Tank Temperature | AV
DifPrAlm | Differential Pressure Alarm | DV
DlgtThr | Daylight Threshold | AV
DmndLmtEna | Demand Limit Enable | DV
DmndLmtLvl | Demand Limit Level | AV
DprAct | Damper Action | DV
DprFbk | Damper Feedback | AI
DprFbk | Damper Feedback | AV
DprLkAlm | Damper Leak Alarm | DV
DprLkAlmSv | Damper Lead Alarm Shunt Variable | DV
DprPos | Damper Position | AO
DprPos | Damper Position | AV
DprTestMd | Damper Test Mode | MV
DrftCalActv | Floating Actuator Drift Compensation Active | DV
DrftCalEna | Floating Actuator Drift Compensation Enable | DV
DrSw | Door Switch | DI
DrSw | Door Switch | DV
DtmpBypDprPos | Dual Temperature Bypass Damper Position | AO
DtmpBypDprPos | Dual Temperature Bypass Damper Position | AV
DtmpMd | Dual Temperature Mode | MV
DtmpPCmd | Dual Temperature Pump Command | DO
DtmpPCmd | Dual Temperature Pump Command | DV
DtmpPSts | Dual Temperature Pump Status | DI
DtmpPSts | Dual Temperature Pump Status | DV
DtmpRTmp | Dual Temperature Return Temperature | AI
DtmpRTmp | Dual Temperature Return Temperature | AV
DtmpSaTmp | Dual Temperature Supply Air Temperature | AI
DtmpSaTmp | Dual Temperature Supply Air Temperature | AV
DtmpSaTmpSpt | Dual Temperature Supply Air Temperature Setpoint | AV
DtmpSTmp | Dual Temperature Supply Temperature | AI
DtmpSTmp | Dual Temperature Supply Temperature | AV
DtmpSwoVlvCmd | Dual Temperature Switchover Valve Command | DO
DtmpSwoVlvCmd | Dual Temperature Switchover Valve Command | DV
DtmpVlvCmd | Dual Temperature Valve Command | DO
DtmpVlvCmd | Dual Temperature Valve Command | DV
DtmpVlvPos | Dual Temperature Valve Position | AO
DtmpVlvPos | Dual Temperature Valve Position | AV
DtmpVlvPosClgLlmt | Dual Temperature Valve Position Cooling Low Limit | AV
DtmpVlvPosHtgLlmt | Dual Temperature Valve Position Heating Low Limit | AV
DxCmpAmp | Direct Expansion Compressor Amps | AI
DxCmpAmp | Direct Expansion Compressor Amps | AV
DxCmpCmd | Direct Expansion Compressor Command | DO
DxCmpCmd | Direct Expansion Compressor Command | DV
DxCmpCmdFof | Direct Expansion Compressor Command Fail Off Alarm | DV
DxCmpCmdFofSv | Direct Expansion Compressor Command Fail Off Alarm Shunt Variable | DV
DxCmpCmdFon | Direct Expansion Compressor Command Fail On Alarm | DV
DxCmpCmdFonSv | Direct Expansion Compressor Command Fail On Alarm Shunt Variable | DV
DxCmpFof | Direct Expansion Compressor Fail Off Alarm | DV
DxCmpFon | Direct Expansion Compressor Fail On Alarm | DV
DxCmpRt | Direct Expansion Compressor Run Time | AV
DxCmpSpd | Direct Expansion Compressor Speed | AO
DxCmpSpd | Direct Expansion Compressor Speed | AV
DxCmpSts | Direct Expansion Compressor Status | DI
DxCmpSts | Direct Expansion Compressor Status | DV
DxCmpStsAmpSptOn | Direct Expansion Compressor Status Amp On Setpoint | AV
DxLoad | Direct Expansion Load | AV
EaBalBoxFl | Exhaust Air Balanced Box Rated Flow | AV
EaBalFlCorFct | Exhaust Air Balanced Box Flow Correction Factor | AV
EaBalKFct | Exhaust Air Balanced k-Factor | AV
EaBoxFlMax | Exhaust Air Maximum Measured Box Flow | AV
EaBoxFlMid | Exhaust Air Intermediate Measured Box Flow | AV
EaBoxFlMin | Exhaust Air Minimum Measured Box Flow | AV
EaClsofTestSts | Exhaust Air Close Off Test Status | MV
EaCO | Exhaust Air Carbon Monoxide | AI
EaCO | Exhaust Air Carbon Monoxide | AV
EaCO2 | Exhaust Air Carbon Dioxide | AI
EaCO2 | Exhaust Air Carbon Dioxide | AV
EaCO2Spt | Exhaust Air Carbon Dioxide Setpoint | AV
EaCOSpt | Exhaust Air Carbon Monoxide Setpoint | AV
EaDew | Exhaust Air Dew Point | AI
EaDew | Exhaust Air Dew Point | AV
EaDprCmd | Exhaust Air Damper Command | DO
EaDprCmd | Exhaust Air Damper Command | DV
EaDprCmdCls | Exhaust Air Damper Close Command | DO
EaDprCmdCls | Exhaust Air Damper Close Command | DV
EaDprCmdOpn | Exhaust Air Damper Open Command | DO
EaDprCmdOpn | Exhaust Air Damper Open Command | DV
EaDprFbk | Exhaust Air Damper Feedback | AI
EaDprFbk | Exhaust Air Damper Feedback | AV
EaDprLkAlm | Exhaust Air Damper Leak Alarm | DV
EaDprLkAlmSv | Exhaust Air Damper Leak Alarm Shunt Variable | DV
EaDprPos | Exhaust Air Damper Position | AO
EaDprPos | Exhaust Air Damper Position | AV
EaDprPosMax | Maximum Exhaust Air Damper Position | AO
EaDprPosMax | Maximum Exhaust Air Damper Position | AV
EaDprPosMin | Minimum Exhaust Air Damper Position | AO
EaDprPosMin | Minimum Exhaust Air Damper Position | AV
EaDprTestMd | Exhaust Air Damper Test Mode | MV
EaEnth | Exhaust Air Enthalpy | AI
EaEnth | Exhaust Air Enthalpy | AV
EaFanAlm | Exhaust Air Fan Alarm | DI
EaFanAlm | Exhaust Air Fan Alarm | DV
EaFanAmp | Exhaust Air Fan Amps | AI
EaFanAmp | Exhaust Air Fan Amps | AV
EaFanAmpFalm | Exhaust Air Fan Amp Fail Alarm | DV
EaFanCmd | Exhaust Air Fan Command | DO
EaFanCmd | Exhaust Air Fan Command | DV
EaFanCmdHi | Exhaust Air Fan High Speed Command | DO
EaFanCmdHi | Exhaust Air Fan High Speed Command | DV
EaFanCmdLo | Exhaust Air Fan Low Speed Command | DO
EaFanCmdLo | Exhaust Air Fan Low Speed Command | DV
EaFanCmdMed | Exhaust Air Fan Medium Speed Command | DO
EaFanCmdMed | Exhaust Air Fan Medium Speed Command | DV
EaFanDifPr | Exhaust Air Fan Differential Pressure | AI
EaFanDifPr | Exhaust Air Fan Differential Pressure | AV
EaFanFbk | Exhaust Air Fan Feedback | AI
EaFanFbk | Exhaust Air Fan Feedback | AV
EaFanFl | Exhaust Air Fan Flow | AI
EaFanFl | Exhaust Air Fan Flow | AV
EaFanFlTot | Exhaust Air Fan Flow Total | AV
EaFanFof | Exhaust Air Fan Fail Off Alarm | DV
EaFanFon | Exhaust Air Fan Fail On Alarm | DV
EaFanFreq | Exhaust Air Fan Frequency | AO
EaFanFreq | Exhaust Air Fan Frequency | AV
EaFanKw | Exhaust Air Fan Kilowatts | AV
EaFanKwh | Exhaust Air Fan Kilowatt-Hours | AV
EaFanRt | Exhaust Air Fan Run Time | AV
EaFanSpd | Exhaust Air Fan Speed | AO
EaFanSpd | Exhaust Air Fan Speed | AV
EaFanSpdFbk | Exhaust Air Fan Speed Feedback | AI
EaFanSpdFbk | Exhaust Air Fan Speed Feedback | AV
EaFanSpdMax | Exhaust Air Fan Maximum Speed | AV
EaFanSpdMin | Exhaust Air Fan Minimum Speed | AV
EaFanSpdSpt | Exhaust Air Fan Speed Setpoint | AV
EaFanSts | Exhaust Air Fan Status | DI
EaFanSts | Exhaust Air Fan Status | DV
EaFanStsHi | Exhaust Air Fan High Speed Status | DI
EaFanStsHi | Exhaust Air Fan High Speed Status | DV
EaFanStsLo | Exhaust Air Fan Low Speed Status | DI
EaFanStsLo | Exhaust Air Fan Low Speed Status | DV
EaFanStsMed | Exhaust Air Fan Medium Speed Status | DI
EaFanStsMed | Exhaust Air Fan Medium Speed Status | DV
EaFanVfdAlm | Exhaust Air Fan Variable Frequency Drive Alarm | DI
EaFanVfdAlm | Exhaust Air Fan Variable Frequency Drive Alarm | DV
EaFanVfdFlt | Exhaust Air Fan Variable Frequency Drive Fault | DI
EaFanVfdFlt | Exhaust Air Fan Variable Frequency Drive Fault | DV
EaFilDifPr | Exhaust Air Filter Differential Pressure | AI
EaFilDifPr | Exhaust Air Filter Differential Pressure | AV
EaFl | Exhaust Air Flow | AI
EaFl | Exhaust Air Flow | AV
EaFl | Exhaust Air Flow | PNEU
EaFlBalMd | Exhaust Air Flow Balance Mode | MV
EaFlCalAlm | Exhaust Air Flow Calibration Alarm | DV
EaFlCalAlmSv | Exhaust Air Flow Calibration Alarm Shunt Variable | DV
EaFlLalm | Exhaust Air Flow Low Alarm | DV
EaFlLalmSv | Exhaust Air Flow Low Alarm Shunt Variable | DV
EaFlLoWrn | Exhaust Air Flow Low Warning | DV
EaFlLoWrnSv | Exhaust Air Flow Low Warning Shunt Variable | DV
EaFlMax | Exhaust Air Flow Max Value | AV
EaFlMaxTestSts | Maximum Exhaust Air Flow Test Status | MV
EaFlMin | Exhaust Air Flow Min Value | AV
EaFlMinTestSts | Minimum Exhaust Air Flow Test Status | MV
EaFlSpt | Exhaust Air Flow Setpoint | AV
EaFlSptClgMax | Maximum Cooling Exhaust Air Flow Setpoint | AV
EaFlSptClgMid | Intermediate Cooling Exhaust Air Flow Setpoint | AV
EaFlSptClgMin | Minimum Cooling Exhaust Air Flow Setpoint | AV
EaFlSptHtgMax | Maximum Heating Exhaust Air Flow Setpoint | AV
EaFlSptHtgMid | Intermediate Heating Exhaust Air Flow Setpoint | AV
EaFlSptHtgMin | Minimum Heating Exhaust Air Flow Setpoint | AV
EaFlSptMax | Maximum Exhaust Air Flow Setpoint | AV
EaFlSptMin | Minimum Exhaust Air Flow Setpoint | AV
EaFlSptOfs | Exhaust Air Flow Setpoint Offset | AV
EaFlTestMd | Exhaust Air Flow Test Mode | MV
EaHoodFlMax | Exhaust Air Maximum Measured Hood Flow | AV
EaHoodFlMid | Exhaust Air Intermediate Measured Hood Flow | AV
EaHoodFlMin | Exhaust Air Minimum Measured Hood Flow | AV
EaNO2 | Exhaust Air Nitrogen Dioxide | AI
EaNO2 | Exhaust Air Nitrogen Dioxide | AV
EaNO2Spt | Exhaust Air Nitrogen Dioxide Setpoint | AV
EaRatedBoxFlow | Exhaust Air Box Rated Flow | AV
EaRatedBoxFlowFalm | Exhaust Air Rated Box Flow Fail Alarm - Must Be Non-Zero | DV
EaRh | Exhaust Air Relative Humidity | AI
EaRh | Exhaust Air Relative Humidity | AV
EaRhSpt | Exhaust Air Relative Humidity Setpoint | AV
EaRlfDprPos | Exhaust Air Relief Damper Position | AO
EaRlfDprPos | Exhaust Air Relief Damper Position | AV
EaStPr | Exhaust Air Static Pressure | AI
EaStPr | Exhaust Air Static Pressure | AV
EaStPrHlmtSw | Exhaust Air Static High Pressure Limit Switch | DI
EaStPrHlmtSw | Exhaust Air Static High Pressure Limit Switch | DV
EaStPrLlmtSw | Exhaust Air Static Low Pressure Limit Switch | DI
EaStPrLlmtSw | Exhaust Air Static Low Pressure Limit Switch | DV
EaStPrSpt | Exhaust Air Static Pressure Setpoint | AV
EaTmp | Exhaust Air Temperature | AI
EaTmp | Exhaust Air Temperature | AV
EaTmpSpt | Exhaust Air Temperature Setpoint | AV
EaVelPr | Exhaust Air Velocity Pressure | AI
EaVelPr | Exhaust Air Velocity Pressure | AV
EaVelPrTestSts | Exhaust Air Velocity Pressure Test Status | MV
EaVlvPos | Exhaust Air Valve Position | AO
EaVlvPos | Exhaust Air Valve Position | AV
EcFl | Evaporative Cooler Flow | AI
EcFl | Evaporative Cooler Flow | AV
EcFlSpt | Evaporative Cooler Flow Setpoint | AV
EcIsoVlvPos | Evaporative Cooler Isolation Valve Position | AO
EcIsoVlvPos | Evaporative Cooler Isolation Valve Position | AV
EcLoad | Evaporative Cooler Load | AV
EconDprFbk | Economizer Damper Feedback | AI
EconDprFbk | Economizer Damper Feedback | AV
EconDprPos | Economizer Damper Position | AO
EconDprPos | Economizer Damper Position | AV
EconDprPosHi | Economizer Damper High Position | AV
EconDprPosLo | Economizer Damper Low Position | AV
EconEna | Economizer Enable | DV
EconEnaOaEnthSpt | Economizer Enable Outside Air Enthalpy Setpoint | AV
EconEnaOaTmpSpt | Economizer Enable Outside Air Temperature Setpoint | AV
EconEnthHlmt | Economizer High Enthalpy Limit | AV
EconLoad | Economizer Load | AV
EconOaDewEnaSpt | Economizer Outside Air Dew Point Enable Setpoint | AV
EconOaEnthEnaSpt | Economizer Outside Air Enthalpy Enable Setpoint | AV
EconRaEnthEnaSpt | Economizer Return Air Enthalpy Enable Setpoint | AV
EconRaTmpEnaSpt | Economizer Return Air Temperature Enable Setpoint | AV
EconTestMd | Economizer Test Mode | MV
EconTmpHlmt | Economizer High Temperature Limit | AV
EcRfgEnth | Evaporative Cooler Refrigerant Enthalpy | AI
EcRfgEnth | Evaporative Cooler Refrigerant Enthalpy | AV
EcRfgPr | Evaporative Cooler Refrigerant Pressure | AI
EcRfgPr | Evaporative Cooler Refrigerant Pressure | AV
EcRfgREnth | Evaporative Cooler Refrigerant Return Enthalpy | AI
EcRfgREnth | Evaporative Cooler Refrigerant Return Enthalpy | AV
EcRfgRTmp | Evaporative Cooler Refrigerant Return Temperature | AI
EcRfgRTmp | Evaporative Cooler Refrigerant Return Temperature | AV
EcRfgTmp | Evaporative Cooler Refrigerant Temperature | AI
EcRfgTmp | Evaporative Cooler Refrigerant Temperature | AV
EcRTmp | Evaporative Cooler Return Temperature | AI
EcRTmp | Evaporative Cooler Return Temperature | AV
EcSTmp | Evaporative Cooler Supply Temperature | AI
EcSTmp | Evaporative Cooler Supply Temperature | AV
EcSTmpSpt | Evaporative Cooler Supply Temperature Setpoint | AV
EcSts | Evaporative Cooler Status | DI
EcSts | Evaporative Cooler Status | DV
EdhSts | Electric Duct Heater Status | DI
EdhSts | Electric Duct Heater Status | DV
EhCmd | Electric Heat Command | DO
EhCmd | Electric Heat Command | DV
EhCmdMinOff | Electric Heat Command Minimum Off Time | AV
EhCmdMinOn | Electric Heat Command Minimum On Time | AV
EhLoad | Electric Heat Load | AV
EhPos | Electric Heat Position | AO
EhPos | Electric Heat Position | AV
EruEaFilDifPr | Energy Recovery Unit Exhaust Air Filter Differential Pressure | AI
EruEaFilDifPr | Energy Recovery Unit Exhaust Air Filter Differential Pressure | AV
EruEaFilDifPrSw | Energy Recovery Unit Exhaust Air Filter Differential Pressure Switch | DI
EruEaFilDifPrSw | Energy Recovery Unit Exhaust Air Filter Differential Pressure Switch | DV
EruEaRh | Energy Recovery Unit Exhaust Air Relative Humidity | AI
EruEaRh | Energy Recovery Unit Exhaust Air Relative Humidity | AV
EruEaTmp | Energy Recovery Unit Exhaust Air Temperature | AI
EruEaTmp | Energy Recovery Unit Exhaust Air Temperature | AV
EruOaBypDprCmd | Energy Recovery Unit Outside Air Bypass Damper Command | DO
EruOaBypDprCmd | Energy Recovery Unit Outside Air Bypass Damper Command | DV
EruOaBypDprPos | Energy Recovery Unit Exhaust Air Bypass Damper Position | AO
EruOaBypDprPos | Energy Recovery Unit Exhaust Air Bypass Damper Position | AV
EruOaFilDifPr | Energy Recovery Unit Outside Air Filter Differential Pressure | AI
EruOaFilDifPr | Energy Recovery Unit Outside Air Filter Differential Pressure | AV
EruOaFilDifPrSw | Energy Recovery Unit Outside Air Filter Differential Pressure Switch | DI
EruOaFilDifPrSw | Energy Recovery Unit Outside Air Filter Differential Pressure Switch | DV
EruOaTmp | Energy Recovery Unit Outside Air Temperature | AI
EruOaTmp | Energy Recovery Unit Outside Air Temperature | AV
EruRaTmp | Energy Recovery Unit Return Air Temperature | AI
EruRaTmp | Energy Recovery Unit Return Air Temperature | AV
EruSaRh | Energy Recovery Unit Supply Air Relative Humidity | AI
EruSaRh | Energy Recovery Unit Supply Air Relative Humidity | AV
EruSaTmp | Energy Recovery Unit Supply Air Temperature | AI
EruSaTmp | Energy Recovery Unit Supply Air Temperature | AV
ErwAlm | Energy Recovery Wheel General Alarm | DI
ErwAlm | Energy Recovery Wheel General Alarm | DV
ErwAmp | Energy Recovery Wheel Amps | AI
ErwAmp | Energy Recovery Wheel Amps | AV
ErwCmd | Energy Recovery Wheel Command | DO
ErwCmd | Energy Recovery Wheel Command | DV
ErwEaBypDprCmd | Energy Recovery Wheel Exhaust Air Bypass Damper Command | DO
ErwEaBypDprCmd | Energy Recovery Wheel Exhaust Air Bypass Damper Command | DV
ErwEaFilDifPr | Energy Recovery Wheel Exhaust Air Filter Differential Pressure | AI
ErwEaFilDifPr | Energy Recovery Wheel Exhaust Air Filter Differential Pressure | AV
ErwEaFilSts | Energy Recovery Relief Filter Switch Status | DI
ErwEaFilSts | Energy Recovery Relief Filter Switch Status | DV
ErwEaRh | Energy Recovery Wheel Exhaust Air Relative Humidity | AI
ErwEaRh | Energy Recovery Wheel Exhaust Air Relative Humidity | AV
ErwEaTmp | Energy Recovery Wheel Exhaust Air Temperature | AI
ErwEaTmp | Energy Recovery Wheel Exhaust Air Temperature | AV
ErwEna | Energy Recovery Wheel Enable | DO
ErwEna | Energy Recovery Wheel Enable | DV
ErwEnaRt | Energy Recovery Wheel Enable Run Time | AV
ErwFreq | Energy Recovery Wheel Frequency | AO
ErwFreq | Energy Recovery Wheel Frequency | AV
ErwKw | Energy Recovery Wheel Kilowatts | AV
ErwKwh | Energy Recovery Wheel Kilowatt-Hours | AV
ErwOaBypDprCmd | Energy Recovery Wheel Outside Air Bypass Damper Command | DO
ErwOaBypDprCmd | Energy Recovery Wheel Outside Air Bypass Damper Command | DV
ErwOaFilDifPr | Energy Recovery Wheel Outside Air Filter Differential Pressure | AI
ErwOaFilDifPr | Energy Recovery Wheel Outside Air Filter Differential Pressure | AV
ErwOaFilDifPrSts | Energy Recovery Wheel Outside Air Filter Differential Pressure Status | DI
ErwOaFilDifPrSts | Energy Recovery Wheel Outside Air Filter Differential Pressure Status | DV
ErwOaFilSts | Energy Recovery Wheel Outside Air Filter Status | DI
ErwOaFilSts | Energy Recovery Wheel Outside Air Filter Status | DV
ErwOaTmp | Energy Recovery Wheel Outside Air Temperature | AI
ErwOaTmp | Energy Recovery Wheel Outside Air Temperature | AV
ErwRaRh | Energy Recovery Wheel Return Air Relative Humidity | AI
ErwRaRh | Energy Recovery Wheel Return Air Relative Humidity | AV
ErwRaTmp | Energy Recovery Wheel Return Air Temperature | AI
ErwRaTmp | Energy Recovery Wheel Return Air Temperature | AV
ErwRotAlm | Energy Recovery Wheel Rotation Alarm | DI
ErwRotAlm | Energy Recovery Wheel Rotation Alarm | DV
ErwSaEnth | Energy Recovery Wheel Supply Air Enthalpy | AI
ErwSaEnth | Energy Recovery Wheel Supply Air Enthalpy | AV
ErwSaRh | Energy Recovery Wheel Supply Air Relative Humidity | AI
ErwSaRh | Energy Recovery Wheel Supply Air Relative Humidity | AV
ErwSaTmp | Energy Recovery Wheel Supply Air Temperature | AI
ErwSaTmp | Energy Recovery Wheel Supply Air Temperature | AV
ErwSpd | Energy Recovery Wheel Speed | AO
ErwSpd | Energy Recovery Wheel Speed | AV
ErwSpdFbk | Energy Recovery Wheel Speed Feedback | AI
ErwSpdFbk | Energy Recovery Wheel Speed Feedback | AV
ErwSts | Energy Recovery Wheel Status | DI
ErwSts | Energy Recovery Wheel Status | DV
ErwVfdAlm | Energy Recovery Wheel Variable Frequency Drive Alarm | DI
ErwVfdAlm | Energy Recovery Wheel Variable Frequency Drive Alarm | DV
ErwVfdFbk | Energy Recovery Wheel Variable Frequency Drive Feedback | AI
ErwVfdFbk | Energy Recovery Wheel Variable Frequency Drive Feedback | AV
ErwVfdSts | Energy Recovery Wheel Variable Frequency Drive Status | DI
ErwVfdSts | Energy Recovery Wheel Variable Frequency Drive Status | DV
ExpTnkPr | Expansion Tank Pressure | AI
ExpTnkPr | Expansion Tank Pressure | AV
ExtLtCmd | Exterior Lighting Command | DO
ExtLtCmd | Exterior Lighting Command | DV
ExtLtCmd | Exterior Lighting Command | LO
ExtLtSts | Exterior Lighting Status | DI
ExtLtSts | Exterior Lighting Status | DV
FanAlm | Fan Alarm | DI
FanAlm | Fan Alarm | DV
FanAmp | Fan Amps | AI
FanAmp | Fan Amps | AV
FanCmd | Fan Command | DO
FanCmd | Fan Command | DV
FanCmdHi | Fan High Speed Command | DO
FanCmdHi | Fan High Speed Command | DV
FanCmdLo | Fan Low Speed Command | DO
FanCmdLo | Fan Low Speed Command | DV
FanCmdMed | Fan Medium Speed Command | DO
FanCmdMed | Fan Medium Speed Command | DV
FanCmdMinOff | Fan Command Minimum Off Time | AV
FanCmdMinOn | Fan Command Minimum On Time | AV
FanCmdReq | Fan Command Request | DV
FanCmdRt | Fan Command Run Time | AV
FanDisDly | Fan Disable Delay | AV
FanDisHwVlvPosSpt | Fan Disable Hot Water Valve Position Setpoint | AV
FanEnaDif | Fan Enable Differential | AV
FanEnaDly | Fan Enable Delay | AV
FanEnaHwVlvPosSpt | Fan Enable Hot Water Valve Position Setpoint | AV
FanEnaSpt | Fan Enable Setpoint | AV
FanFof | Fan Fail Off Alarm | DV
FanFofSv | Fan Fail Off Alarm Shunt Variable | DV
FanFon | Fan Fail On Alarm | DV
FanFonSv | Fan Fail On Alarm Shunt Variable | DV
FanFreq | Fan Frequency | AO
FanFreq | Fan Frequency | AV
FanKw | Fan Kilowatts | AV
FanKwh | Fan Kilowatt-Hours | AV
FanMd | Fan Mode | MV
FanOnWu | Fan on Warmup | DV
FanRt | Fan Run Time | AV
FanSel | Fan Selector | MV
FanSpd | Fan Speed | AO
FanSpd | Fan Speed | AV
FanSpdFbk | Fan Speed Feedback | AI
FanSpdFbk | Fan Speed Feedback | AV
FanSpdSpt | Fan Speed Setpoint | AV
FanSts | Fan Status | DI
FanSts | Fan Status | DV
FanStsHi | Fan High Speed Status | DI
FanStsHi | Fan High Speed Status | DV
FanStsLo | Fan Low Speed Status | DI
FanStsLo | Fan Low Speed Status | DV
FanStsMed | Fan Medium Speed Status | DI
FanStsMed | Fan Medium Speed Status | DV
FanStsRt | Fan Status Run Time | AV
FanTestMd | Fan Test Mode | MV
FanTestSts | Fan Test Status | MV
FanUnocRt | Fan Unoccupied Run Time | AV
FanVfdAlm | Fan Variable Frequency Drive Alarm | DI
FanVfdAlm | Fan Variable Frequency Drive Alarm | DV
FbDprOaEnaSpt | Face and Bypass Damper Outside Air Temperature Enable Setpoint | AV
FbDprOaTmpLocSpt | Face and Bypass Damper Outside Air Temperature Lockout Setpoint | AV
FbDprPos | Face and Bypass Damper Position | AO
FbDprPos | Face and Bypass Damper Position | AV
FfilAlm | Final Filter Alarm | DI
FfilAlm | Final Filter Alarm | DV
FfilDifPr | Final Filter Differential Pressure | AI
FfilDifPr | Final Filter Differential Pressure | AV
FfilDifPrSw | Final Filter Differential Pressure Switch | DI
FfilDifPrSw | Final Filter Differential Pressure Switch | DV
FhAirFl | Fume Hood Air Flow | AI
FhAirFl | Fume Hood Air Flow | AV
FhAirFl | Fume Hood Air Flow | PNEU
FhAirFlSpt | Fume Hood Air Flow Setpoint | AV
FhAlm | Fume Hood Alarm | DI
FhAlm | Fume Hood Alarm | DV
FhSashPos | Fume Hood Sash Position | AI
FhSashPos | Fume Hood Sash Position | AV
FhVelPr | Fume Hood Velocity Pressure | AI
FhVelPr | Fume Hood Velocity Pressure | AV
FilAlm | Filter Alarm | DI
FilAlm | Filter Alarm | DV
FilAlmSv | Filter Alarm Shunt Variable | DV
FilDifPr | Filter Differential Pressure | AI
FilDifPr | Filter Differential Pressure | AV
FilDifPrSw | Filter Differential Pressure Switch | DI
FilDifPrSw | Filter Differential Pressure Switch | DV
FilSts | Filter Status | DI
FilSts | Filter Status | DV
FilStsDifPrSptOn | Filter Status Differential Pressure On Setpoint | AV
FireAlm | Fire Alarm | DI
FireAlm | Fire Alarm | DV
FltSts | Fault Status | DV
FrstDetAlm | Frost Detector Alarm | DI
FrstDetAlm | Frost Detector Alarm | DV
FrstProt | Frost Protection | DV
FrzTmp | Freezer Temperature | AI
FrzTmp | Freezer Temperature | AV
FzAlmLvl | Freeze Alarm Level | DV
FzAlmLvlSv | Freeze Alarm Level Shunt Variable | DV
FzDif | Freeze Differential | AV
FzMdDon | Freeze Mode Delay On | AV
FzSbDif | Freeze Setback Differential | AV
FzSbSpt | Freeze Setback Setpoint | AV
FzSpt | Freeze Setpoint | AV
GasCostRate | Gas Cost Rate | AV
GasKw | Gas Kilowatts | AV
GasKwh | Gas Kilowatt-Hours | AV
GasPr | Gas Pressure | AI
GasPr | Gas Pressure | AV
GasUseRate | Gas Use Rate | AV
GblLoc | Global Lockout | DV
GblRtRst | Global Run Time Reset | DV
GenAlm | Generator Alarm | DI
GenAlm | Generator Alarm | DV
GenGasFl | Generator Gas Flow | AI
GenGasFl | Generator Gas Flow | AV
GenGasKw | Generator Gas Kilowatts | AV
GenGasKwh | Generator Gas Kilowatt-Hours | AV
GenKw | Generator Electrical Kilowatts | AV
GenKwh | Generator Electrical Kilowatt-Hours | AV
GenKwSpt | Generator Kilowatt Setpoint | AV
GenSts | Generator Status | DI
GenSts | Generator Status | DV
GenVlvPos | Generator Valve Position | AO
GenVlvPos | Generator Valve Position | AV
GhCmd | Gas Heat Stage Command | DO
GhCmd | Gas Heat Stage Command | DV
GhCmdMinOff | Gas Heat Command Minimum Off Time | AV
GhCmdMinOn | Gas Heat Command Minimum On Time | AV
GhLoad | Gas Heat Load | AV
GhPos | Gas Heat Position | AO
GhPos | Gas Heat Position | AV
GrgCO | Garage Carbon Monoxide | AI
GrgCO | Garage Carbon Monoxide | AV
HdAhuWu | Air Handling Unit Hot Deck Warmup | DV
HdAirFl | Hot Deck Air Flow | AI
HdAirFl | Hot Deck Air Flow | AV
HdAirFl | Hot Deck Air Flow | PNEU
HdAirFlBalMd | Hot Deck Air Flow Balance Mode | MV
HdAirFlCalAlm | Hot Deck Air Flow Calibration Alarm | DV
HdAirFlCalAlmSv | Hot Deck Air Flow Calibration Alarm Shunt Variable | DV
HdAirFlFalm | Hot Deck Air Flow Fail Alarm | DV
HdAirFlHalm | Hot Deck Air Flow High Alarm | DV
HdAirFlLalm | Hot Deck Air Flow Low Alarm | DV
HdAirFlLalmSv | Hot Deck Air Flow Low Alarm Shunt Variable | DV
HdAirFlLoWrn | Hot Deck Air Flow Low Warning | DV
HdAirFlLoWrnSv | Hot Deck Air Flow Low Warning Shunt Variable | DV
HdAirFlMaxTestSts | Maximum Hot Deck Air Flow Test Status | MV
HdAirFlMinTestSts | Minimum Hot Deck Air Flow Test Status | MV
HdAirFlSpt | Hot Deck Air Flow Setpoint | AV
HdAirFlSptMax | Maximum Hot Deck Air Flow Setpoint | AV
HdAirFlSptMid | Intermediate Hot Deck Air Flow Setpoint | AV
HdAirFlSptMin | Minimum Hot Deck Air Flow Setpoint | AV
HdAirFlTestMd | Hot Deck Air Flow Test Mode | MV
HdBalFlCorFct | Hot Deck Balanced Box Flow Correction Factor | AV
HdBalKFct | Hot Deck Balanced k-Factor | AV
HdBoxFlMax | Hot Deck Maximum Measured Box Flow | AV
HdBoxFlMid | Hot Deck Medium Measured Box Flow | AV
HdBoxFlMin | Hot Deck Minimum Measured Box Flow | AV
HdBoxFlRated | Hot Deck Box Rated Flow | AV
HdBoxFlRatedFalm | Hot Deck Rated Box Flow Fail Alarm | DV
HdClsofTestSts | Hot Deck Close Off Test Status | MV
HdDprCmd | Hot Deck Damper Command | DO
HdDprCmd | Hot Deck Damper Command | DV
HdDprFbk | Hot Deck Damper Feedback | AO
HdDprFbk | Hot Deck Damper Feedback | AV
HdDprLkAlm | Hot Deck Damper Leak Alarm | DV
HdDprLkAlmSv | Hot Deck Damper Lead Alarm Shunt Variable | DV
HdDprPos | Hot Deck Damper Position | AO
HdDprPos | Hot Deck Damper Position | AV
HdDprTestMd | Hot Deck Damper Test Mode | MV
HdFanReq | Hot Deck Fan Request | AV
HdFanReqHalm | Hot Deck Fan Request High Alarm | DV
HdFanReqHalmSv | Hot Deck Fan Request High Alarm Shunt Variable | DV
HdFanReqPct | Hot Deck Fan Request Hours as Percent | AV
HdFanReqRst | Hot Deck Fan Reset Request Hours Reset | DV
HdFanReqRt | Hot Deck Fan Request Hours | AV
HdHoodFlMax | Hot Deck Maximum Measured Hood Flow | AV
HdHoodFlMid | Hot Deck Medium Measured Hood Flow | AV
HdHoodFlMin | Hot Deck Minimum Measured Hood Flow | AV
HdRatedBoxFlowFalm | Hot Deck Rated Box Flow Fail Alarm - Must Be Non-Zero | DV
HdStPr | Hot Deck Static Pressure | AI
HdStPr | Hot Deck Static Pressure | AV
HdStPrRstReq | Hot Deck Static Pressure Reset Requests | AV
HdStPrRstReqHalm | Hot Deck Static Pressure Reset Request High Alarm | DV
HdStPrRstReqHalmSv | Hot Deck Static Pressure Reset Request High Alarm Shunt Variable | DV
HdStPrRstReqPct | Hot Deck Static Pressure Reset Request Hours as Percent | AV
HdStPrRstReqRst | Hot Deck Static Pressure Reset Request Hours Reset | DV
HdStPrRstReqRt | Hot Deck Static Pressure Reset Request Hours | AV
HdTmaVntClsTml | Hot Deck Time-Averaged Close Time Left | AV
HdTmaVntOpnTml | Hot Deck Time-Averaged Open Time Left | AV
HdTmaVntSts | Hot Deck Time-Averaged Ventilation Status | DV
HdTmp | Hot Deck Temperature | AI
HdTmp | Hot Deck Temperature | AV
HdVelPr | Hot Deck Velocity Pressure | AI
HdVelPr | Hot Deck Velocity Pressure | AV
HdVelPrTestSts | Hot Deck Velocity Pressure Test Stage | MV
HhwVlvCmd | Heating Hot Water Valve Command | DO
HhwVlvCmd | Heating Hot Water Valve Command | DV
HhwVlvFbk | Heating Hot Water Valve Feedback | AI
HhwVlvFbk | Heating Hot Water Valve Feedback | AV
HhwVlvPos | Heating Hot Water Valve Position | AO
HhwVlvPos | Heating Hot Water Valve Position | AV
HoodFlMax | Maximum Measured Hood Flow | AV
HoodFlMid | Intermediate Measured Hood Flow | AV
HoodFlMin | Minimum Measured Hood Flow | AV
HpCmd | Heat Pump Command | DO
HpCmd | Heat Pump Command | DV
HpStgNum | Number of Heat Pump Compressor Stages | AV
HpSts | Heat Pump Status | DI
HpSts | Heat Pump Status | DV
HrAlm | Heat Recovery Alarm | DI
HrAlm | Heat Recovery Alarm | DV
HrBypDprPos | Heat Recovery Bypass Damper Position | AO
HrBypDprPos | Heat Recovery Bypass Damper Position | AV
HrBypVlvPos | Heat Recovery Bypass Valve Position | AO
HrBypVlvPos | Heat Recovery Bypass Valve Position | AV
HrCmd | Heat Recovery Command | DO
HrCmd | Heat Recovery Command | DV
HrDifPr | Heat Recovery Differential Pressure | AI
HrDifPr | Heat Recovery Differential Pressure | AV
HrDifPrSpt | Heat Recovery Differential Pressure Setpoint | AV
HrEaBypDprCmd | Heat Recovery Exhaust Air Bypass Damper Command | DO
HrEaBypDprCmd | Heat Recovery Exhaust Air Bypass Damper Command | DV
HrEaBypDprPos | Heat Recovery Exhaust Air Bypass Damper Position | AO
HrEaBypDprPos | Heat Recovery Exhaust Air Bypass Damper Position | AV
HrEaFbDprPos | Heat Recovery Exhaust Air Face and Bypass Damper Position | AO
HrEaFbDprPos | Heat Recovery Exhaust Air Face and Bypass Damper Position | AV
HrEaFilDifPr | Heat Recovery Exhaust Air Filter Differential Pressure | AI
HrEaFilDifPr | Heat Recovery Exhaust Air Filter Differential Pressure | AV
HrEaFilSts | Heat Recovery Exhaust Filter Switch Status | DI
HrEaFilSts | Heat Recovery Exhaust Filter Switch Status | DV
HrEaRh | Heat Recovery Exhaust Air Relative Humidity | AI
HrEaRh | Heat Recovery Exhaust Air Relative Humidity | AV
HrEaRTmp | Heat Recovery Exhaust Air Return Temperature | AI
HrEaRTmp | Heat Recovery Exhaust Air Return Temperature | AV
HrEaTmp | Heat Recovery Exhaust Air Temperature | AI
HrEaTmp | Heat Recovery Exhaust Air Temperature | AV
HrEaTmpSpt | Heat Recovery Exhaust Air Temperature Setpoint | AV
HrEf | Heat Recovery Efficiency | AV
HrFbDprPos | Heat Recovery Face and Bypass Damper Position | AO
HrFbDprPos | Heat Recovery Face and Bypass Damper Position | AV
HrFl | Heat Recovery Flow | AI
HrFl | Heat Recovery Flow | AV
HrHtgSaTmp | Heat Recovery Heating Supply Air Temperature | AI
HrHtgSaTmp | Heat Recovery Heating Supply Air Temperature | AV
HrIsoVlvPos | Heat Recovery Isolation Valve Position | AO
HrIsoVlvPos | Heat Recovery Isolation Valve Position | AV
HrOaBypDprCmd | Energy Recovery Outside Air Bypass Damper Command | DO
HrOaBypDprCmd | Energy Recovery Outside Air Bypass Damper Command | DV
HrOaFilDifPr | Energy Recovery Outside Air Filter Differential Pressure | AI
HrOaFilDifPr | Energy Recovery Outside Air Filter Differential Pressure | AV
HrOaFilSts | Energy Recovery Outside Air Filter Status | DI
HrOaFilSts | Energy Recovery Outside Air Filter Status | DV
HrPAmp | Heat Recovery Pump Amps | AI
HrPAmp | Heat Recovery Pump Amps | AV
HrPclSaTmp | Heat Recovery Precool Supply Air Temperature | AI
HrPclSaTmp | Heat Recovery Precool Supply Air Temperature | AV
HrPCmd | Heat Recovery Pump Command | DO
HrPCmd | Heat Recovery Pump Command | DV
HrPFreq | Heat Recovery Pump Frequency | AI
HrPFreq | Heat Recovery Pump Frequency | AV
HrPKw | Heat Recovery Pump Kilowatts | AV
HrPKwh | Heat Recovery Pump Kilowatt-Hours | AV
HrPSpd | Heat Recovery Pump Speed | AO
HrPSpd | Heat Recovery Pump Speed | AV
HrPSpdFbk | Heat Recovery Speed Feedback | AI
HrPSpdFbk | Heat Recovery Speed Feedback | AV
HrPSts | Heat Recovery Pump Status | DI
HrPSts | Heat Recovery Pump Status | DV
HrRaRh | Heat Recovery Return Air Relative Humidity | AI
HrRaRh | Heat Recovery Return Air Relative Humidity | AV
HrRaTmp | Heat Recovery Return Air Temperature | AI
HrRaTmp | Heat Recovery Return Air Temperature | AV
HrRTmp | Heat Recovery Return Water Temperature | AI
HrRTmp | Heat Recovery Return Water Temperature | AV
HrRTmpSpt | Heat Recovery Return Temperature Setpoint | AV
HrSaRh | Heat Recovery Supply Air Relative Humidity | AI
HrSaRh | Heat Recovery Supply Air Relative Humidity | AV
HrSaTmp | Energy Recovery Supply Air Temperature | AI
HrSaTmp | Energy Recovery Supply Air Temperature | AV
HrSaTmpSpt | Heat Recovery Supply Air Temperature Setpoint | AV
HrSTmp | Heat Recovery Supply Water Temperature | AI
HrSTmp | Heat Recovery Supply Water Temperature | AV
HrSTmpSpt | Heat Recovery Supply Temperature Setpoint | AV
HrSts | Heat Recovery Status | DI
HrSts | Heat Recovery Status | DV
HrVlvPos | Heat Recovery Valve Position | AO
HrVlvPos | Heat Recovery Valve Position | AV
HrwAlm | Heat Recovery Wheel Alarm | DI
HrwAlm | Heat Recovery Wheel Alarm | DV
HrwAmp | Heat Recovery Wheel Amps | AI
HrwAmp | Heat Recovery Wheel Amps | AV
HrwCmd | Heat Recovery Wheel Command | DO
HrwCmd | Heat Recovery Wheel Command | DV
HrwEaBypDprCmd | Heat Recovery Wheel Exhaust Air Bypass Damper Command | DO
HrwEaBypDprCmd | Heat Recovery Wheel Exhaust Air Bypass Damper Command | DV
HrwEaFilDifPr | Heat Recovery Wheel Exhaust Air Filter Differential Pressure | AI
HrwEaFilDifPr | Heat Recovery Wheel Exhaust Air Filter Differential Pressure | AV
HrwEaFilSts | Heat Recovery Wheel Exhaust Filter Status | DI
HrwEaFilSts | Heat Recovery Wheel Exhaust Filter Status | DV
HrwEaRh | Heat Recovery Wheel Exhaust Air Relative Humidity | AI
HrwEaRh | Heat Recovery Wheel Exhaust Air Relative Humidity | AV
HrwEaTmp | Heat Recovery Wheel Exhaust Air Temperature | AI
HrwEaTmp | Heat Recovery Wheel Exhaust Air Temperature | AV
HrwEna | Heat Recovery Wheel Enable | DV
HrwFreq | Heat Recovery Wheel Frequency | AO
HrwFreq | Heat Recovery Wheel Frequency | AV
HrwKw | Heat Recovery Wheel Kilowatts | AV
HrwKwh | Heat Recovery Wheel Kilowatt-Hours | AV
HrwOaBypDprCmd | Heat Recovery Wheel Outside Air Bypass Damper Command | DO
HrwOaBypDprCmd | Heat Recovery Wheel Outside Air Bypass Damper Command | DV
HrwOaFilDifPr | Heat Recovery Wheel Outside Air Filter Differential Pressure | AI
HrwOaFilDifPr | Heat Recovery Wheel Outside Air Filter Differential Pressure | AV
HrwOaFilSts | Heat Recovery Wheel Outside Air Filter Status | DI
HrwOaFilSts | Heat Recovery Wheel Outside Air Filter Status | DV
HrwSaRh | Heat Recovery Wheel Supply Air Relative Humidity | AI
HrwSaRh | Heat Recovery Wheel Supply Air Relative Humidity | AV
HrwSaTmp | Heat Recovery Wheel Supply Air Temperature | AI
HrwSaTmp | Heat Recovery Wheel Supply Air Temperature | AV
HrwSpd | Heat Recovery Wheel Speed | AO
HrwSpd | Heat Recovery Wheel Speed | AV
HrwSpdFbk | Heat Recovery Wheel Speed Feedback | AI
HrwSpdFbk | Heat Recovery Wheel Speed Feedback | AV
HrwSts | Heat Recovery Wheel Status | DI
HrwSts | Heat Recovery Wheel Status | DV
HrwVfdAlm | Heat Recovery Wheel Variable Frequency Drive Alarm | DI
HrwVfdAlm | Heat Recovery Wheel Variable Frequency Drive Alarm | DV
HrwVfdFbk | Heat Recovery Wheel Variable Frequency Drive Feedback | AI
HrwVfdFbk | Heat Recovery Wheel Variable Frequency Drive Feedback | AV
HrwVfdSts | Heat Recovery Wheel Variable Frequency Drive Status | DI
HrwVfdSts | Heat Recovery Wheel Variable Frequency Drive Status | DV
HtgAlm | Heating Alarm | DI
HtgAlm | Heating Alarm | DV
HtgAmp | Heating Amps | AI
HtgAmp | Heating Amps | AV
HtgBypDprPos | Heating Bypass Damper Position | AO
HtgBypDprPos | Heating Bypass Damper Position | AV
HtgCall | Heating Call | DV
HtgClgMd | Heating/Cooling Mode | MV
HtgClgSts | Heating/Cooling Status | MV
HtgCmd | Heating Command | DO
HtgCmd | Heating Command | DV
HtgCmdStg | Heating Command Stage | DO
HtgCmdStg | Heating Command Stage | DV
HtgCph | Heating Cycles per Hour | AV
HtgDchrgTmpAvg | Heating Discharge Air Temperature Average | AV
HtgDmnd | Heating Demand | AV
HtgEntTmpAvg | Heating Entering Air Temperature Average | AV
HtgHwRTmp | Heating Hot Water Return Temperature | AI
HtgHwRTmp | Heating Hot Water Return Temperature | AV
HtgKw | Heating Kilowatts | AV
HtgKwh | Heating Kilowatt-Hours | AV
HtgLoad | Heating Load | AV
HtgMd | Heating Mode | MV
HtgOaTmpLocSpt | Heating Outside Air Temperature Lockout Setpoint | AV
HtgPCmd | Heating Pump Command | DO
HtgPCmd | Heating Pump Command | DV
HtgPos | Heating Position | AO
HtgPos | Heating Position | AV
HtgPSts | Heating Pump Status | DI
HtgPSts | Heating Pump Status | DV
HtgRstReq | Heating Reset Request | AV
HtgRstReqHalm | Heating Reset Request High Alarm | DV
HtgRstReqHalmSv | Heating Reset Request High Alarm Shunt Variable | DV
HtgRstReqPct | Heating Reset Request Hours as Percent | AV
HtgRstReqRst | Heating Reset Request Hours Reset | DV
HtgRstReqRt | Heating Reset Request Hours | AV
HtgRTmp | Heating Return Water Temperature | AI
HtgRTmp | Heating Return Water Temperature | AV
HtgSaTmp | Heating Supply Air Temperature | AI
HtgSaTmp | Heating Supply Air Temperature | AV
HtgSaTmpAvg | Heating Supply Air Temperature Average | AV
HtgSaTmpSpt | Heating Supply Air Temperature Setpoint | AV
HtgStgNum | Number of Heating Stages | AV
HtgSTmp | Heating Supply Water Temperature | AI
HtgSTmp | Heating Supply Water Temperature | AV
HtgSts | Heating Status | DI
HtgSts | Heating Status | DV
HtgTestMd | Heating Test Mode | MV
HtgTestSts | Heating Test Status | MV
HtgVlvFbk | Heating Valve Feedback | AI
HtgVlvFbk | Heating Valve Feedback | AV
HtgVlvPos | Heating Valve Position | AO
HtgVlvPos | Heating Valve Position | AV
HumAlm | Humidifier Alarm | DI
HumAlm | Humidifier Alarm | DV
HumCmd | Humidifier Command | DO
HumCmd | Humidifier Command | DV
HumDmnd | Humidifier Demand | AO
HumDmnd | Humidifier Demand | AV
HumEna | Humidifier Enable | DO
HumEna | Humidifier Enable | DV
HumIsoVlvCmd | Humidifier Isolation Valve Command | DO
HumIsoVlvCmd | Humidifier Isolation Valve Command | DV
HumMd | Humidifier Mode | MV
HumPos | Humidifier Position | AV
HumRhSpt | Humidifier Relative Humidity Setpoint | AV
HumSts | Humidifier Status | DI
HumSts | Humidifier Status | DV
HumTestMd | Humidifier Test Mode | MV
HumVlvFbk | Humidifier Valve Feedback | AI
HumVlvFbk | Humidifier Valve Feedback | AV
HumVlvPos | Humidifier Valve Position | AO
HumVlvPos | Humidifier Valve Position | AV
HvacSts | HVAC Status | MV
HwBlrGasFlMain | Main Boiler Gas Flow | AI
HwBlrGasFlMain | Main Boiler Gas Flow | AV
HwBypAlm | Hot Water Bypass Alarm | DV
HwBypFl | Hot Water Bypass Flow | AI
HwBypFl | Hot Water Bypass Flow | AV
HwBypFlDir | Hot Water Bypass Flow Direction | DV
HwBypTmp | Hot Water Bypass Temperature | AI
HwBypTmp | Hot Water Bypass Temperature | AV
HwBypVlvFbk | Hot Water Bypass Valve Feedback | AI
HwBypVlvFbk | Hot Water Bypass Valve Feedback | AV
HwBypVlvPos | Hot Water Bypass Valve Position | AO
HwBypVlvPos | Hot Water Bypass Valve Position | AV
HwCapActl | Hot Water Capacity Actual | AV
HwCapActlAvg | Hot Water Capacity Actual Rolling Average | AV
HwCapReq | Hot Water Capacity Required | AV
HwCapReqAvg | Hot Water Capacity Required Rolling Average | AV
HwDcpFl | Hot Water Decoupler Flow | AI
HwDcpFl | Hot Water Decoupler Flow | AV
HwDcpTmp | Hot Water Decoupler Temperature | AI
HwDcpTmp | Hot Water Decoupler Temperature | AV
HwDifPr | Hot Water Differential Pressure | AI
HwDifPr | Hot Water Differential Pressure | AV
HwDifPrAlm | Hot Water Differential Pressure Alarm | DV
HwDifPrCalAlm | Hot Water Differential Pressure Calibration Alarm | DV
HwDifPrErrThr | Hot Water Differential Pressure Error Threshold | AV
HwDifPrSpt | Hot Water Differential Pressure Setpoint | AV
HwDifPrSptMax | Hot Water Differential Pressure Setpoint Maximum | AV
HwDifPrSptMin | Hot Water Differential Pressure Setpoint Minimum | AV
HwExpTnkPr | Hot Water Expansion Tank Pressure | AI
HwExpTnkPr | Hot Water Expansion Tank Pressure | AV
HwFl | Hot Water Flow | AI
HwFl | Hot Water Flow | AV
HwFlDir | Hot Water Flow Direction | MV
HwFlErrThr | Hot Water Flow Error Threshold | AV
HwFlFalm | Hot Water Flow Fail Alarm | DV
HwFlHalm | Hot Water Flow High Alarm | DV
HwFlLalm | Hot Water Flow Low Alarm | DV
HwIsoVlvPos | Hot Water Isolation Valve Position | AO
HwIsoVlvPos | Hot Water Isolation Valve Position | AV
HwMuwFl | Hot Water Makeup Water Flow | AI
HwMuwFl | Hot Water Makeup Water Flow | AV
HwPAmp | Hot Water Pump Amps | AI
HwPAmp | Hot Water Pump Amps | AV
HwPCmd | Hot Water Pump Command | DO
HwPCmd | Hot Water Pump Command | DV
HwPLd | Hot Water Pump Lead | AV
HwPRt | Hot Water Pump Run Time | AV
HwPSpd | Hot Water Pump Speed | AO
HwPSpd | Hot Water Pump Speed | AV
HwPSpdFbk | Hot Water Pump Speed Feedback | AI
HwPSpdFbk | Hot Water Pump Speed Feedback | AV
HwPSts | Hot Water Pump Status | DI
HwPSts | Hot Water Pump Status | DV
HwRadVlvCmd | Hot Water Radiation Valve Command | DO
HwRadVlvCmd | Hot Water Radiation Valve Command | DV
HwRadVlvPos | Hot Water Radiation Valve Position | AO
HwRadVlvPos | Hot Water Radiation Valve Position | AV
HwReqPct | Hot Water Request Hours as Percent | AV
HwReqRst | Hot Water Request Hours Reset | DV
HwReqRt | Hot Water Request Hours | AV
HwRFl | Hot Water Return Flow | AI
HwRFl | Hot Water Return Flow | AV
HwRFlAlm | Hot Water Return Flow Alarm | DV
HwRFlCalAlm | Hot Water Return Flow Calibration Alarm | DV
HwRFlSpt | Hot Water Return Flow Setpoint | AI
HwRFlSpt | Hot Water Return Flow Setpoint | AV
HwRFlSptDsn | Hot Water Return Flow Design Setpoint | AI
HwRFlSptDsn | Hot Water Return Flow Design Setpoint | AV
HwRFlSptMin | Hot Water Return Flow Minimum Setpoint | AI
HwRFlSptMin | Hot Water Return Flow Minimum Setpoint | AV
HwRPr | Hot Water Return Pressure | AI
HwRPr | Hot Water Return Pressure | AV
HwRstReq | Hot Water Reset Requests | AV
HwRstReqPct | Hot Water Reset Request Hours Percentage | AV
HwRstReqRst | Hot Water Reset Request Hours Reset | DV
HwRstReqRt | Hot Water Reset Request Hours | AV
HwRTmp | Hot Water Return Temperature | AI
HwRTmp | Hot Water Return Temperature | AV
HwRTmpFalm | Hot Water Return Temperature Fail Alarm | DV
HwRTmpHalm | Hot Water Return Temperature High Alarm | DV
HwRTmpLalm | Hot Water Return Temperature Low Alarm | DV
HwSFl | Hot Water Supply Flow | AI
HwSFl | Hot Water Supply Flow | AV
HwSPr | Hot Water Supply Pressure | AI
HwSPr | Hot Water Supply Pressure | AV
HwSTmp | Hot Water Supply Temperature | AI
HwSTmp | Hot Water Supply Temperature | AV
HwSTmpAlm | Hot Water Supply Temperature Alarm | DV
HwSTmpAlmSv | Hot Water Supply Temperature Alarm Shunt Variable | DV
HwSTmpFalm | Hot Water Supply Temperature Fail Alarm | DV
HwSTmpHalm | Hot Water Supply Temperature High Alarm | DV
HwSTmpLalm | Hot Water Supply Temperature Low Alarm | DV
HwSTmpSpt | Hot Water Supply Temperature Setpoint | AV
HwSTmpSptMax | Hot Water Supply Temperature Maximum Setpoint | AV
HwSTmpSptMin | Hot Water Supply Temperature Minimum Setpoint | AV
HwSTmpSptRstDlyDn | Hot Water Supply Temperature Setpoint Reset Delay Down | AV
HwSTmpSptRstDlyUp | Hot Water Supply Temperature Setpoint Reset Delay Up | AV
HwSTmpSptTestMdAlm | Hot Water Supply Temperature Setpoint Reset Test Mode Alarm | DV
HwSysAlmInh | Hot Water System Alarm Inhibit | DV
HwSysAlmRst | Hot Water System Master Alarm Reset | DV
HwSysAvl | Hot Water System Available | DV
HwSysEna | Hot Water System Enable | DV
HwSysGblRtRst | Hot Water System Global Run Time Reset | DV
HwSysOaTmpLocSpt | Hot Water System Outside Air Temperature Lockout Setpoint | AV
HwSysPr | Hot Water System Pressure | AI
HwSysPr | Hot Water System Pressure | AV
HwSysReq | Hot Water System Request | AV
HwSysReqCnt | Hot Water System Request Count | AV
HwSysReqIgnCnt | Hot Water System Ignored Request Count | AV
HwSysReqPct | Hot Water System Request Hours as Percent | AV
HwSysReqRst | Hot Water System Request Hours Reset | DV
HwSysReqRt | Hot Water System Request Hours | AV
HwSysRstReqCnt | Hot Water System Reset Request Count | AV
HwSysRstReqIgnCnt | Hot Water System Ignored Reset Request Count | AV
HwSysStgFireRateMin | Hot Water System Stage Minimum Firing Rate | AV
HwSysSts | Hot Water System Status | DV
HwTmpErrThr | Hot Water Temperature Error Threshold | AV
HwVlvCmd | Hot Water Valve Command | DO
HwVlvCmd | Hot Water Valve Command | DV
HwVlvCmdCls | Hot Water Valve Command Close | DO
HwVlvCmdCls | Hot Water Valve Command Close | DV
HwVlvCmdMinOff | Hot Water Valve Command Minimum Off Time | AV
HwVlvCmdMinOn | Hot Water Valve Command Minimum On Time | AV
HwVlvCmdOpn | Hot Water Valve Command Open | DO
HwVlvCmdOpn | Hot Water Valve Command Open | DV
HwVlvFbk | Hot Water Valve Feedback | AI
HwVlvFbk | Hot Water Valve Feedback | AV
HwVlvLoad | Hot Water Valve Load | AV
HwVlvPos | Hot Water Valve Position | AO
HwVlvPos | Hot Water Valve Position | AV
HwVlvPosAvg | Average Hot Water Valve Position | AV
HwVlvPosHi | Highest Hot Water Valve Position | AV
HwVlvPosLo | Lowest Hot Water Valve Position | AV
HxAlm | Heat Exchanger Alarm | DI
HxAlm | Heat Exchanger Alarm | DV
HxBypVlvPos | Heat Exchanger Bypass Valve Position | AO
HxBypVlvPos | Heat Exchanger Bypass Valve Position | AV
HxChgVlvCmd | Heat Exchanger Changeover Valve Command | DO
HxChgVlvCmd | Heat Exchanger Changeover Valve Command | DV
HxChgVlvPos | Heat Exchanger Changeover Valve Position | AO
HxChgVlvPos | Heat Exchanger Changeover Valve Position | AV
HxChwSVlvPos | Heat Exchanger Chilled Water Supply Valve Position | AO
HxChwSVlvPos | Heat Exchanger Chilled Water Supply Valve Position | AV
HxCmd | Heat Exchanger Command | DO
HxCmd | Heat Exchanger Command | DV
HxFl | Heat Exchanger Flow | AI
HxFl | Heat Exchanger Flow | AV
HxHrSVlvPos | Heat Exchanger Heat Recovery Supply Valve Position | AO
HxHrSVlvPos | Heat Exchanger Heat Recovery Supply Valve Position | AV
HxHwSVlvFbk | Heat Exchanger Hot Water Supply Valve Feedback | AI
HxHwSVlvFbk | Heat Exchanger Hot Water Supply Valve Feedback | AV
HxHwSVlvPos | Heat Exchanger Hot Water Supply Valve Position | AO
HxHwSVlvPos | Heat Exchanger Hot Water Supply Valve Position | AV
HxIsoVlvPos | Heat Exchanger Isolation Valve Position | AO
HxIsoVlvPos | Heat Exchanger Isolation Valve Position | AV
HxOaTmpEnaSpt | Heat Exchanger Outside Air Temperature Enable Setpoint | AV
HxRTmp | Heat Exchanger Return Temperature | AI
HxRTmp | Heat Exchanger Return Temperature | AV
HxSTmp | Heat Exchanger Supply Temperature | AI
HxSTmp | Heat Exchanger Supply Temperature | AV
HxSTmpSpt | Heat Exchanger Supply Temperature Setpoint | AV
HxStmSVlvPos | Heat Exchanger Steam Supply Valve Position | AO
HxStmSVlvPos | Heat Exchanger Steam Supply Valve Position | AV
IgvDprPos | Inlet Guide Vane Damper Position | AO
IgvDprPos | Inlet Guide Vane Damper Position | AV
ImpMult | Importance Multiplier | AV
ImpMultClg | Cooling Importance Multiplier | AV
ImpMultHtg | Heating Importance Multiplier | AV
ImpMultStPr | Static Pressure Importance Multiplier | AV
IntruderAlm | Intruder Alarm | DV
KeyCrdSts | Key Card Status | DI
KeyCrdSts | Key Card Status | DV
KpLoc | Keypad Lockout | DV
KwhPul | Kilowatt-Hour Pulse | DI
KwhPul | Kilowatt-Hour Pulse | DV
KwPul | Kilowatt Pulse | DI
KwPul | Kilowatt Pulse | DV
LclLoc | Local Lockout | DV
LclWu | Local Warmup | DV
LclWuMdDif | Local Warmup Mode Differential | AV
LclWuMdDof | Local Warmup Mode Delay Off | AV
LclWuMdOfs | Local Warmup Mode Offset | AV
LkAlm | Leak Alarm | DI
LkAlm | Leak Alarm | DV
LpsPr | Low Pressure Steam Pressure | AI
LpsPr | Low Pressure Steam Pressure | AV
LpsSFl | Low Pressure Steam Supply Flow | AI
LpsSFl | Low Pressure Steam Supply Flow | AV
LtCmd | Lighting Command | DO
LtCmd | Lighting Command | DV
LtCmd | Lighting Command | LO
LtCmdHi | Lighting High Command | DO
LtCmdHi | Lighting High Command | DV
LtCmdHi | Lighting High Command | LO
LtCmdLo | Lighting Low Command | DO
LtCmdLo | Lighting Low Command | DV
LtCmdLo | Lighting Low Command | LO
LtEna | Lighting Enable | DO
LtEna | Lighting Enable | DV
LtEna | Lighting Enable | LO
LtLvl | Lighting Level | AV
LtLvlOut | Light Level Output | AO
LtLvlOut | Light Level Output | AV
LtLvlScn | Lighting Level Scene | AV
LtSts | Lighting Status | DI
LtSts | Lighting Status | DV
MaDew | Mixed Air Dew Point | AI
MaDew | Mixed Air Dew Point | AV
MaFfilAlm | Mixed Air Final Filter Alarm | DI
MaFfilAlm | Mixed Air Final Filter Alarm | DV
MaFfilAlmSv | Mixed Air Final Filter Alarm Shunt Variable | DV
MaFfilDifPr | Mixed Air Final Filter Differential Pressure | AI
MaFfilDifPr | Mixed Air Final Filter Differential Pressure | AV
MaFfilDifPrHlmt | Mixed Air Final Filter Differential Pressure High Limit | AV
MaFfilSts | Mixed Air Final Filter Status | DI
MaFfilSts | Mixed Air Final Filter Status | DV
MainBkrKw | Main Breaker Kilowatts | AI
MainBkrKw | Main Breaker Kilowatts | AV
MainBkrKwh | Main Breaker Kilowatt-Hours | AI
MainBkrKwh | Main Breaker Kilowatt-Hours | AV
MaintMd | Maintenance Mode | DV
MaintMdAlm | Maintenance Mode Alarm | DV
MaintMdAlmSv | Maintenance Mode Alarm Shunt Variable | DV
MaintReqAlm | Maintenance Request Alarm | DV
MaintReqAlmSv | Maintenance Request Alarm Shunt Variable | DV
MaintReqRtRst | Maintenance Request Run Time Reset | DV
MaLmt | Mixed Air Limit | AV
ManLd | Manual Lead | AV
ManLg | Manual Lag | AV
MaPfilAlm | Mixed Air Pre-Filter Alarm | DI
MaPfilAlm | Mixed Air Pre-Filter Alarm | DV
MaPfilAlmSv | Mixed Air Pre-Filter Alarm Shunt Variable | DV
MaPfilDifPr | Mixed Air Pre-Filter Differential Pressure | AI
MaPfilDifPr | Mixed Air Pre-Filter Differential Pressure | AV
MaPfilDifPrHlmt | Mixed Air Pre-Filter Differential Pressure High Limit | AV
MaPfilSts | Mixed Air Pre-Filter Status | DI
MaPfilSts | Mixed Air Pre-Filter Status | DV
MaRh | Mixed Air Relative Humidity | AI
MaRh | Mixed Air Relative Humidity | AV
MaStPr | Mixed Air Static Pressure | AI
MaStPr | Mixed Air Static Pressure | AV
MaStPrSpt | Mixed Air Static Pressure Setpoint | AV
MaTmp | Mixed Air Temperature | AI
MaTmp | Mixed Air Temperature | AV
MaTmpAvg | Average Mixed Air Temperature | AV
MaTmpFalm | Mixed Air Temperature Fail Alarm | DV
MaTmpFalmSv | Mixed Air Temperature Fail Alarm Shunt Variable | DV
MaTmpHalm | Mixed Air Temperature High Alarm | DV
MaTmpHi | Highest Mixed Air Temperature | AI
MaTmpHi | Highest Mixed Air Temperature | AV
MaTmpHlmt | Mixed Air Temperature High Limit | AV
MaTmpLalm | Mixed Air Temperature Low Alarm | DV
MaTmpLlmt | Mixed Air Temperature Low Limit | AV
MaTmpLo | Lowest Mixed Air Temperature | AI
MaTmpLo | Lowest Mixed Air Temperature | AV
MaTmpMin | Minimum Mixed Air Temperature | AV
MaTmpSpt | Mixed Air Temperature Setpoint | AV
MaTmpSptUnoc | Unoccupied Mixed Air Setpoint | AV
MaTmpTestSts | Mixed Air Temperature Test Status | MV
MixVlvPos | Mixing Valve Position | AO
MixVlvPos | Mixing Valve Position | AV
MoaDifPr | Minimum Outside Air Differential Pressure | AI
MoaDifPr | Minimum Outside Air Differential Pressure | AV
MoaDifPrFalm | Minimum Outside Air Differential Pressure Fail Alarm | DV
MoaDifPrFalmSv | Minimum Outside Air Differential Pressure Fail Alarm Shunt Variable | DV
MoaDifPrSpt | Minimum Outside Air Differential Pressure Setpoint | AV
MoaDifPrSptDsn | Minimum Outside Air Differential Pressure Design Setpoint | AV
MoaDifPrTestSts | Minimum Outside Air Differential Pressure Test Status | MV
MoaDprCmd | Minimum Outside Air Damper Command | DO
MoaDprCmd | Minimum Outside Air Damper Command | DV
MoaDprCmdCls | Minimum Outside Air Damper Close Command | DO
MoaDprCmdCls | Minimum Outside Air Damper Close Command | DV
MoaDprCmdOpn | Minimum Outside Air Damper Open Command | DO
MoaDprCmdOpn | Minimum Outside Air Damper Open Command | DV
MoaDprEsw | Minimum Outside Air Damper End Switch | DI
MoaDprEsw | Minimum Outside Air Damper End Switch | DV
MoaDprFbk | Minimum Outside Air Damper Feedback | AI
MoaDprFbk | Minimum Outside Air Damper Feedback | AV
MoaDprOaTmpLlmt | Minimum Outside Air Damper Outside Air Temperature Low Limit | AV
MoaDprOpnSts | Minimum Outside Air Damper Open Status | DI
MoaDprOpnSts | Minimum Outside Air Damper Open Status | DV
MoaDprPos | Minimum Outside Air Damper Position | AO
MoaDprPos | Minimum Outside Air Damper Position | AV
MoaDprPosSpt | Minimum Outside Air Damper Position Setpoint | AV
MoaDuctArea | Minimum Outside Air Duct Area | AV
MoaFl | Minimum Outside Air Flow | AI
MoaFl | Minimum Outside Air Flow | AV
MoaFl | Minimum Outside Air Flow | PNEU
MoaFlFalm | Minimum Outside Air Flow Fail Alarm | DV
MoaFlFalmSv | Minimum Outside Air Flow Fail Alarm Shunt Variable | DV
MoaFlSpt | Minimum Outside Air Flow Setpoint | AV
MoaFlSptDsn | Minimum Outside Air Flow Design Setpoint | AV
MoaFlSptDsnUncor | Minimum Outside Air Flow Design Uncorrected Setpoint | AV
MoaFlSptMax | Maximum Minimum Outside Air Flow Setpoint | AV
MoaFlSptMaxSpdMax | Minimum Outside Air Damper Position for Design Ventilation at Maximum Fan Speed | AV
MoaFlSptMaxSpdMin | Minimum Outside Air Damper Position for Design Ventilation at Minimum Fan Speed | AV
MoaFlSptMin | Lowest Allowable Minimum Outside Air Flow Setpoint | AV
MoaFlSptMinBldg | Minimum Outside Air Flow Setpoint Building Minimum | AV
MoaFlSptMinOcc | Minimum Outside Air Flow Setpoint Occupancy Minimum | AV
MoaFlSptMinSpdMax | Minimum Outside Air Damper Position for Minimum Ventilation at Maximum Fan Speed | AV
MoaFlSptMinSpdMin | Minimum Outside Air Damper Position for Minimum Ventilation at Minimum Fan Speed | AV
MoaFlTestSts | Minimum Outside Air Flow Test Status | MV
MoaLoad | Minimum Outside Air Load | AV
MoaPct | Minimum Outside Air Percent | AV
MtrRTmp | Meter Return Temperature | AI
MtrRTmp | Meter Return Temperature | AV
MtrSTmp | Meter Supply Temperature | AI
MtrSTmp | Meter Supply Temperature | AV
MuwTmp | Makeup Water Temperature | AI
MuwTmp | Makeup Water Temperature | AV
NO2Alm | Nitrogen Dioxide Alarm | DI
NO2Alm | Nitrogen Dioxide Alarm | DV
NO2Max | Maximum Nitrogen Dioxide | AV
OaCO | Outside Air Carbon Monoxide | AI
OaCO | Outside Air Carbon Monoxide | AV
OaCO2 | Outside Air Carbon Dioxide | AI
OaCO2 | Outside Air Carbon Dioxide | AV
OaDew | Outside Air Dew Point | AI
OaDew | Outside Air Dew Point | AV
OaDprCmd | Outside Air Damper Command | DO
OaDprCmd | Outside Air Damper Command | DV
OaDprCmdCls | Outside Air Damper Close Command | DO
OaDprCmdCls | Outside Air Damper Close Command | DV
OaDprCmdOpn | Outside Air Damper Open Command | DO
OaDprCmdOpn | Outside Air Damper Open Command | DV
OaDprFbk | Outside Air Damper Feedback | AI
OaDprFbk | Outside Air Damper Feedback | AV
OaDprFbkFalm | Outside Air Damper Feedback Fail Alarm | DV
OaDprPos | Outside Air Damper Position | AO
OaDprPos | Outside Air Damper Position | AV
OaDprPosMax | Outside Air Damper Position Maximum | AV
OaDprPosMin | Outside Air Damper Position Minimum | AV
OaDuctArea | Outside Air Duct Area | AV
OaEnth | Outside Air Enthalpy | AI
OaEnth | Outside Air Enthalpy | AV
OaFanCmd | Outside Air Fan Command | DO
OaFanCmd | Outside Air Fan Command | DV
OaFanSpd | Outside Air Fan Speed | AO
OaFanSpd | Outside Air Fan Speed | AV
OaFanSpdFbk | Outside Air Fan Speed Feedback | AI
OaFanSpdFbk | Outside Air Fan Speed Feedback | AV
OaFanSts | Outside Air Fan Status | DI
OaFanSts | Outside Air Fan Status | DV
OaFl | Outside Air Flow | AI
OaFl | Outside Air Flow | AV
OaFl | Outside Air Flow | PNEU
OaFlFalm | Outside Air Flow Fail Alarm | DV
OaFlHalm | Outside Air Flow High Alarm | DV
OaFlLalm | Outside Air Flow Low Alarm | DV
OaFlSpt | Outside Air Flow Setpoint | AV
OaFlSptMax | Outside Air Flow Maximum Setpoint | AV
OaFlSptMin | Outside Air Flow Minimum Setpoint | AV
OaFlTestSts | Outside Air Flow Test Status | MV
OaLoc | Outside Air Lockout | DV
OaLocSpt | Outside Air Lockout Setpoint | AV
OaPct | Outside Air Percent | AV
OaRh | Outside Air Relative Humidity | AI
OaRh | Outside Air Relative Humidity | AV
OaRhFalm | Outside Air Relative Humidity Fail Alarm | DV
OaRhFalmSv | Outside Air Relative Humidity Fail Alarm Shunt Variable | DV
OaSTmpRstHi | Outside Air Supply Temperature Reset High Value | AV
OaSTmpRstLo | Outside Air Supply Temperature Reset Low Value | AV
OaTmp | Outside Air Temperature | AI
OaTmp | Outside Air Temperature | AV
OaTmpAvg | Average Outside Air Temperature | AV
OaTmpAvgCalc | Average Outside Air Temperature Calculated | AV
OaTmpFalm | Outside Air Temperature Fail Alarm | DV
OaTmpFalmSv | Outside Air Temperature Fail Alarm Shunt Variable | DV
OaTmpHalm | Outside Air Temperature High Alarm | DV
OaTmpHlmt | Outside Air Temperature High Limit | AV
OaTmpLalm | Outside Air Temperature Low Alarm | DV
OaTmpTestSts | Outside Air Temperature Test Status | MV
OaVelPr | Outside Air Velocity Pressure | AI
OaVelPr | Outside Air Velocity Pressure | AV
OaWb | Outside Air Wet Bulb | AI
OaWb | Outside Air Wet Bulb | AV
OccCmd | Occupancy Command | DV
OccCmdRt | Occupancy Command Run Time | AV
OccOvr | Occupancy Override | DI
OccOvr | Occupancy Override | DV
OccOvr | Occupancy Override | SS
OccOvrTml | Occupancy Override Time Left | AV
OccSnsr | Occupancy Sensor | DI
OccSnsr | Occupancy Sensor | DV
OccSnsr | Occupancy Sensor | SS
OccSnsrDof | Occupancy Sensor Delay Off | AV
OccSnsrEna | Occupancy Sensor Enable | DV
OccSnsrSts | Occupancy Sensor Status | DI
OccSnsrSts | Occupancy Sensor Status | DV
OccSnsrSts | Occupancy Sensor Status | SS
OccSrc | Occupancy Source | MV
OccSts | Occupancy Status | MV
OperSts | Operation Status | MV
OperStsCnt | Operation Status Count | AV
OptStrtClgEna | Optimal Start Cooling Enable | DV
OptStrtClgMaxTm | Optimal Start Cooling Maximum Time | AV
OptStrtClgRt | Optimal Start Cooling Run Time | AV
OptStrtHtgEna | Optimal Start Heating Enable | DV
OptStrtHtgMaxTm | Optimal Start Heating Maximum Time | AV
OptStrtHtgRt | Optimal Start Heating Run Time | AV
OvrTm | Override Time | AV
PchwDifPr | Primary Chilled Water Differential Pressure | AI
PchwDifPr | Primary Chilled Water Differential Pressure | AV
PchwDifPrSpt | Primary Chilled Water Differential Pressure Setpoint | AV
PchwDifPrVlvPos | Primary Chilled Water Differential Pressure Valve Position | AO
PchwDifPrVlvPos | Primary Chilled Water Differential Pressure Valve Position | AV
PchwFl | Primary Chilled Water Flow | AI
PchwFl | Primary Chilled Water Flow | AV
PchwFlCalAlm | Primary Chilled Water Flow Calibration Alarm | DV
PchwFlSpt | Primary Chilled Water Flow Setpoint | AV
PchwMixVlvPos | Primary Chilled Water Mixing Valve Position | AO
PchwMixVlvPos | Primary Chilled Water Mixing Valve Position | AV
PchwPAmp | Primary Chilled Water Pump Amps | AI
PchwPAmp | Primary Chilled Water Pump Amps | AV
PchwPCmd | Primary Chilled Water Pump Command | DO
PchwPCmd | Primary Chilled Water Pump Command | DV
PchwPCmdDof | Primary Chilled Water Pump Command Delay Off | AV
PchwPCmdDon | Primary Chilled Water Pump Command Delay On | AV
PchwPCmdOvrAlm | Primary Chilled Water Pump Command Forced By Operator Alarm | DV
PchwPDifPr | Primary Chilled Water Pump Differential Pressure | AI
PchwPDifPr | Primary Chilled Water Pump Differential Pressure | AV
PchwPDifPrSpt | Primary Chilled Water Pump Differential Pressure Setpoint | AV
PchwPEna | Primary Chilled Water Pump Enable | DV
PchwPEnaDof | Primary Chilled Water Pump Enable Delay Off | AV
PchwPEnaDon | Primary Chilled Water Pump Enable Delay On | AV
PchwPFbk | Primary Chilled Water Pump Feedback | AI
PchwPFbk | Primary Chilled Water Pump Feedback | AV
PchwPFl | Primary Chilled Water Pump Flow | AI
PchwPFl | Primary Chilled Water Pump Flow | AV
PchwPFof | Primary Chilled Water Pump Fail Off Alarm | DV
PchwPFon | Primary Chilled Water Pump Fail On Alarm | DV
PchwPFreq | Primary Chilled Water Pump Frequency | AO
PchwPFreq | Primary Chilled Water Pump Frequency | AV
PchwPKw | Primary Chilled Water Pump Kilowatts | AI
PchwPKw | Primary Chilled Water Pump Kilowatts | AV
PchwPKwh | Primary Chilled Water Pump Kilowatt-Hours | AV
PchwPKwMax | Primary Chilled Water Pump Kilowatt Maximum | AV
PchwPKwTot | Primary Chilled Water Pump Kilowatts Total | AV
PchwPLclLoc | Primary Chilled Water Pump Local Lockout | DV
PchwPLclLocRst | Primary Chilled Water Pump Local Lockout Reset | DV
PchwPLd | Primary Chilled Water Pump Lead | AV
PchwPLdMan | Primary Chilled Water Pump Lead Manual | AV
PchwPLdRotTs | Primary Chilled Water Pump Lead Rotation Schedule | AV
PchwPLg | Primary Chilled Water Pump Lag Order | AV
PchwPLgDof | Primary Chilled Water Pump Lag Delay Off | AV
PchwPLgDon | Primary Chilled Water Pump Lag Delay On | AV
PchwPLgMan | Primary Chilled Water Pump Lag Manual | AV
PchwPMaintMd | Primary Chilled Water Pump Maintenance Mode | DV
PchwPMaintMdAlm | Primary Chilled Water Pump Maintenance Mode Alarm | DV
PchwPMaintReqAlm | Primary Chilled Water Pump Maintenance Request Alarm | DV
PchwPMaintReqRtRst | Primary Chilled Water Pump Maintenance Request Run Time Reset | DV
PchwPNumAvl | Number of Primary Chilled Water Pumps Available | AV
PchwPNumLclLoc | Number of Primary Chilled Water Pumps In Local Lockout | AV
PchwPNumOvrOn | Number of Primary Chilled Water Pumps Which Are Overridden On | AV
PchwPNumReq | Number of Primary Chilled Water Pumps Request | AV
PchwPNumRun | Number of Primary Chilled Water Pumps Running | AV
PchwPOvrOn | Primary Chilled Water Pump Overridden On | DV
PchwPRotCmdTs | Primary Chilled Water Pump Rotation From Time Schedule | DV
PchwPRotLdMan | Primary Chilled Water Pump Manual Lead Rotation | DV
PchwPRotLdMd | Primary Chilled Water Pump Lead Rotation Mode | MV
PchwPRotOrdManValid | Primary Chilled Water Pump Manual Rotation Order Valid | DV
PchwPRotOrdValid | Primary Chilled Water Pump Rotation Order Valid | DV
PchwPRotSel | Primary Chilled Water Pump Rotation Mode Select | MV
PchwPRotSelfCor | Primary Chilled Water Pump Rotation Self Correcting Option | DV
PchwPRotSw | Primary Chilled Water Pump Rotation Switch | DV
PchwPRotTsFrcRot | Primary Chilled Water Rotation Time Schedule Force Rotation Option | DV
PchwPRt | Primary Chilled Water Pump Run Time | AV
PchwPRtRst | Primary Chilled Water Pump Run Time Reset | DV
PchwPSpd | Primary Chilled Water Pump Speed | AO
PchwPSpd | Primary Chilled Water Pump Speed | AV
PchwPSpdFbk | Primary Chilled Water Pump Speed Feedback | AI
PchwPSpdFbk | Primary Chilled Water Pump Speed Feedback | AV
PchwPSpdHlmt | Primary Chilled Water Pump Speed High Limit | AV
PchwPSpdLlmt | Primary Chilled Water Pump Speed Low Limit | AV
PchwPSpdMin | Primary Chilled Water Pump Minimum Speed | AV
PchwPSpdOvrAlm | Primary Chilled Water Pump Speed Forced By Operator Alarm | DV
PchwPSpdStrt | Primary Chilled Water Pump Startup Speed | AV
PchwPStrtTm | Primary Chilled Water Pump Startup Time | AV
PchwPSts | Primary Chilled Water Pump Status | DI
PchwPSts | Primary Chilled Water Pump Status | DV
PchwPStsOvrAlm | Primary Chilled Water Pump Status Forced By Operator Alarm | DV
PchwPVfdAlm | Primary Chilled Water Pump Variable Frequency Drive Alarm | DI
PchwPVfdAlm | Primary Chilled Water Pump Variable Frequency Drive Alarm | DV
PchwPXrt | Primary Chilled Water Pump Extended Run Time | AV
PchwRFlCalAlm | Primary Chilled Water Return Flow Calibration Alarm | DV
PchwRPr | Primary Chilled Water Return Pressure | AI
PchwRPr | Primary Chilled Water Return Pressure | AV
PchwRTmp | Primary Chilled Water Return Temperature | AI
PchwRTmp | Primary Chilled Water Return Temperature | AV
PchwRTmpSpt | Primary Chilled Water Return Temperature Setpoint | AV
PchwSFl | Primary Chilled Water Supply Flow | AI
PchwSFl | Primary Chilled Water Supply Flow | AV
PchwSFlCalAlm | Primary Chilled Water Supply Flow Calibration Alarm | DV
PchwSPr | Primary Chilled Water Supply Pressure | AI
PchwSPr | Primary Chilled Water Supply Pressure | AV
PchwSPrSpt | Primary Chilled Water Supply Pressure Setpoint | AV
PchwSTmp | Primary Chilled Water Supply Temperature | AI
PchwSTmp | Primary Chilled Water Supply Temperature | AV
PchwSTmpLlmt | Primary Chilled Water Supply Temperature Low Limit | AV
PchwSTmpSpt | Primary Chilled Water Supply Temperature Setpoint | AV
PchwTh | Primary Chilled Water Tons-Hour | AV
PclTmp | Precool Temperature | AI
PclTmp | Precool Temperature | AV
PclVlvPos | Precool Valve Position | AO
PclVlvPos | Precool Valve Position | AV
PDifPr | Pump Differential Pressure | AI
PDifPr | Pump Differential Pressure | AV
PDifPrSpt | Pump Differential Pressure Setpoint | AV
PfilAlm | Pre-Filter Alarm | DI
PfilAlm | Pre-Filter Alarm | DV
PfilDifPr | Pre-Filter Differential Pressure | AI
PfilDifPr | Pre-Filter Differential Pressure | AV
PfilDifPrSw | Pre-Filter Differential Pressure Switch | DI
PfilDifPrSw | Pre-Filter Differential Pressure Switch | DV
PhtBrnrGasVlvPos | Preheat Burner Gas Valve Position | AO
PhtBrnrGasVlvPos | Preheat Burner Gas Valve Position | AV
PhtBypDprPos | Preheat Bypass Damper Position | AO
PhtBypDprPos | Preheat Bypass Damper Position | AV
PhtCmd | Preheat Command | DO
PhtCmd | Preheat Command | DV
PhtFbDprPos | Preheat Face and Bypass Damper Position | AO
PhtFbDprPos | Preheat Face and Bypass Damper Position | AV
PhtLoad | Preheat Load | AV
PhtOaEnaSpt | Preheat Outside Air Temperature Enable Setpoint | AV
PhtRTmp | Preheat Return Water Temperature | AI
PhtRTmp | Preheat Return Water Temperature | AV
PhtRTmpSpt | Preheat Return Temperature Setpoint | AV
PhtSaRh | Preheat Supply Relative Humidity | AI
PhtSaRh | Preheat Supply Relative Humidity | AV
PhtSaTmp | Preheat Supply Air Temperature | AI
PhtSaTmp | Preheat Supply Air Temperature | AV
PhtSaTmpAvg | Preheat Supply Air Temperature Average | AV
PhtSaTmpSpt | Preheat Supply Air Temperature Setpoint | AV
PhtStgCmd | Preheat Stage Command | DO
PhtStgCmd | Preheat Stage Command | DV
PhtSTmp | Preheat Supply Water Temperature | AI
PhtSTmp | Preheat Supply Water Temperature | AV
PhtTmp | Preheat Discharge Temperature | AI
PhtTmp | Preheat Discharge Temperature | AV
PhtTmpAlmSpt | Preheat Temperature Alarm Setpoint | AV
PhtVlvCmd | Preheat Valve Command | DO
PhtVlvCmd | Preheat Valve Command | DV
PhtVlvFbk | Preheat Valve Feedback | AI
PhtVlvFbk | Preheat Valve Feedback | AV
PhtVlvPos | Preheat Valve Modulation | AO
PhtVlvPos | Preheat Valve Modulation | AV
PhwDifPr | Primary Hot Water Differential Pressure | AI
PhwDifPr | Primary Hot Water Differential Pressure | AV
PhwDifPrSpt | Primary Hot Water Differential Pressure Setpoint | AV
PhwDifPrVlvPos | Primary Hot Water Differential Pressure Valve Position | AO
PhwDifPrVlvPos | Primary Hot Water Differential Pressure Valve Position | AV
PhwFl | Primary Hot Water Flow | AI
PhwFl | Primary Hot Water Flow | AV
PhwFlAlm | Primary Hot Water Flow Alarm | DV
PhwFlCalAlm | Primary Hot Water Flow Calibration Alarm | DV
PhwFlSpt | Primary Hot Water Flow Setpoint | AV
PhwFlSptDsn | Primary Hot Water Design Flow Setpoint | AV
PhwHtgKw | Primary Hot Water Heating Kilowatts | AV
PhwHtgKwh | Primary Hot Water Heating Kilowatt-Hours | AV
PhwMixVlvPos | Primary Hot Water Mixing Valve Position | AO
PhwMixVlvPos | Primary Hot Water Mixing Valve Position | AV
PhwPAmp | Primary Hot Water Pump Amps | AI
PhwPAmp | Primary Hot Water Pump Amps | AV
PhwPCmd | Primary Hot Water Pump Command | DO
PhwPCmd | Primary Hot Water Pump Command | DV
PhwPDifPr | Primary Hot Water Pump Differential Pressure | AI
PhwPDifPr | Primary Hot Water Pump Differential Pressure | AV
PhwPDifPrSpt | Primary Hot Water Pump Differential Pressure Setpoint | AV
PhwPEna | Primary Hot Water Pump Enable | DV
PhwPFbk | Primary Hot Water Pump Feedback | AI
PhwPFbk | Primary Hot Water Pump Feedback | AV
PhwPFl | Primary Hot Water Pump Flow | AI
PhwPFl | Primary Hot Water Pump Flow | AV
PhwPFof | Primary Hot Water Pump Fail Off Alarm | DV
PhwPFon | Primary Hot Water Pump Fail On Alarm | DV
PhwPFreq | Primary Hot Water Pump Frequency | AO
PhwPFreq | Primary Hot Water Pump Frequency | AV
PhwPKw | Primary Hot Water Pump Kilowatts | AV
PhwPKwh | Primary Hot Water Pump Kilowatt-Hours | AV
PhwPLclLoc | Primary Hot Water Pump Local Lockout | DV
PhwPLclLocRst | Primary Hot Water Pump Local Lockout Reset | DV
PhwPLd | Primary Hot Water Pump Lead | AV
PhwPLdMan | Primary Hot Water Pump Lead Manual | AV
PhwPLg | Primary Hot Water Pump Lag | AV
PhwPLgMan | Primary Hot Water Pump Lag Manual | AV
PhwPMaintMd | Primary Hot Water Pump Maintenance Mode | DV
PhwPMaintMdAlm | Primary Hot Water Pump Maintenance Mode Alarm | DV
PhwPMaintReqAlm | Primary Hot Water Pump Maintenance Request | DV
PhwPMaintReqRtRst | Primary Hot Water Pump Maintenance Request Run Time Reset | DV
PhwPNumAvl | Number of Primary Hot Water Pumps Available | AV
PhwPNumLclLoc | Number of Primary Hot Water Pumps In Local Lockout | AV
PhwPNumOvrOn | Number of Primary Hot Water Pumps Which Are Overridden On | AV
PhwPNumReq | Number of Primary Hot Water Pumps Requested | AV
PhwPOvrOn | Primary Hot Water Pump Overridden On | DV
PhwPRotCmdTs | Primary Hot Water Pump Rotation Command From Time Schedule | DV
PhwPRotOrdManValid | Primary Hot Water Pump Manual Rotation Order Valid | DV
PhwPRotOrdValid | Primary Hot Water Pump Rotation Order Valid | DV
PhwPRotSel | Primary Hot Water Pump Rotation Selection | MV
PhwPRotSelfCor | Primary Hot Water Pump Rotation Self Correcting Option | DV
PhwPRotSw | Primary Hot Water Pump Rotation Switch | DV
PhwPRotTsFrcRot | Primary Hot Water Rotation Time Schedule Force Rotation Option | DV
PhwPRt | Primary Hot Water Pump Run Time | AV
PhwPRtRst | Primary Hot Water Pump Run Time Reset | DV
PhwPSpd | Primary Hot Water Pump Speed | AO
PhwPSpd | Primary Hot Water Pump Speed | AV
PhwPSpdFbk | Primary Hot Water Pump Speed Feedback | AI
PhwPSpdFbk | Primary Hot Water Pump Speed Feedback | AV
PhwPSpdMin | Primary Hot Water Pump Minimum Speed | AV
PhwPSts | Primary Hot Water Pump Status | DI
PhwPSts | Primary Hot Water Pump Status | DV
PhwPVfdAlm | Primary Hot Water Pump Variable Frequency Drive Alarm | DI
PhwPVfdAlm | Primary Hot Water Pump Variable Frequency Drive Alarm | DV
PhwPXrt | Primary Hot Water Pump Extended Run Time | AV
PhwRFl | Primary Hot Water Return Flow | AI
PhwRFl | Primary Hot Water Return Flow | AV
PhwRFlCalAlm | Primary Hot Water Return Flow Calibration Alarm | DV
PhwRFlSpt | Primary Hot Water Return Flow Setpoint | AV
PhwRFlSptDsn | Primary Hot Water Return Flow Design Setpoint | AV
PhwRTmp | Primary Hot Water Return Temperature | AI
PhwRTmp | Primary Hot Water Return Temperature | AV
PhwRTmpSpt | Primary Hot Water Return Temperature Setpoint | AV
PhwSFl | Primary Hot Water Supply Flow | AI
PhwSFl | Primary Hot Water Supply Flow | AV
PhwSFlAlm | Primary Hot Water Supply Flow Alarm | DV
PhwSFlAlmSv | Primary Hot Water Supply Flow Alarm Shunt Variable | DV
PhwSFlCalAlm | Primary Hot Water Supply Flow Calibration Alarm | DV
PhwSFlSpt | Primary Hot Water Supply Flow Setpoint | AV
PhwSFlSptDsn | Primary Hot Water Supply Flow Design Setpoint | AV
PhwSTmp | Primary Hot Water Supply Temperature | AI
PhwSTmp | Primary Hot Water Supply Temperature | AV
PhwSTmpAlm | Primary Hot Water Supply Temperature Alarm | DV
PhwSTmpAlmSv | Primary Hot Water Supply Temperature Alarm Shunt Variable | DV
PhwSTmpSpt | Primary Hot Water Supply Temperature Setpoint | AV
PipeNumCfg | Number of Pipe Configuration Selector | MV
PstmFl | Primary Steam Flow | AI
PstmFl | Primary Steam Flow | AV
PstmPr | Primary Steam Pressure | AI
PstmPr | Primary Steam Pressure | AV
PstmPrSpt | Primary Steam Pressure Setpoint | AV
PstmSTmp | Primary Steam Supply Temperature | AI
PstmSTmp | Primary Steam Supply Temperature | AV
PstmSTmpSpt | Primary Steam Supply Temperature Setpoint | AV
PwrDon | Power Delay On | AV
RaCO | Return Air Carbon Monoxide | AI
RaCO | Return Air Carbon Monoxide | AV
RaCO2 | Return Air Carbon Dioxide | AI
RaCO2 | Return Air Carbon Dioxide | AV
RaCO2Dif | Return Air Carbon Dioxide Differential | AI
RaCO2Dif | Return Air Carbon Dioxide Differential | AV
RaCO2Spt | Return Air Carbon Dioxide Setpoint | AV
RaCODif | Return Air Carbon Monoxide Differential | AI
RaCODif | Return Air Carbon Monoxide Differential | AV
RaCOSpt | Return Air Carbon Monoxide Setpoint | AV
RaDew | Return Air Dew Point | AI
RaDew | Return Air Dew Point | AV
RaDewSpt | Return Air Dew Point Setpoint | AV
RaDprCmd | Return Air Damper Command | DO
RaDprCmd | Return Air Damper Command | DV
RaDprCmdCls | Return Air Damper Close Command | DO
RaDprCmdCls | Return Air Damper Close Command | DV
RaDprCmdOpn | Return Air Damper Open Command | DO
RaDprCmdOpn | Return Air Damper Open Command | DV
RaDprFbk | Return Air Damper Feedback | AI
RaDprFbk | Return Air Damper Feedback | AV
RaDprPos | Return Air Damper Position | AO
RaDprPos | Return Air Damper Position | AV
RaEnth | Return Air Enthalpy | AI
RaEnth | Return Air Enthalpy | AV
RaFanAlm | Return Air Fan Alarm | DI
RaFanAlm | Return Air Fan Alarm | DV
RaFanAmp | Return Air Fan Amps | AI
RaFanAmp | Return Air Fan Amps | AV
RaFanAmpFalm | Return Air Fan Amp Fail Alarm | DV
RaFanAryIsoDprCmd | Return Air Fan Array Isolation Damper Command | DO
RaFanAryIsoDprCmd | Return Air Fan Array Isolation Damper Command | DV
RaFanCmd | Return Air Fan Command | DO
RaFanCmd | Return Air Fan Command | DV
RaFanCmdHi | Return Air Fan High Speed Command | DO
RaFanCmdHi | Return Air Fan High Speed Command | DV
RaFanCmdLo | Return Air Fan Low Speed Command | DO
RaFanCmdLo | Return Air Fan Low Speed Command | DV
RaFanCmdMed | Return Air Fan Medium Speed Command | DO
RaFanCmdMed | Return Air Fan Medium Speed Command | DV
RaFanFbk | Return Air Fan Feedback | AI
RaFanFbk | Return Air Fan Feedback | AV
RaFanFl | Return Air Fan Flow | AI
RaFanFl | Return Air Fan Flow | AV
RaFanFof | Return Air Fan Fail Off Alarm | DV
RaFanFofSv | Return Air Fan Fail Off Alarm Shunt Variable | DV
RaFanFon | Return Air Fan Fail On Alarm | DV
RaFanFonSv | Return Air Fan Fail On Alarm Shunt Variable | DV
RaFanFreq | Return Air Fan Frequency | AO
RaFanFreq | Return Air Fan Frequency | AV
RaFanKw | Return Air Fan Kilowatts | AV
RaFanKwh | Return Air Fan Kilowatt-Hours | AV
RaFanOvr | Return Air Fan Override | DV
RaFanRt | Return Air Fan Run Time | AV
RaFanSpd | Return Air Fan Speed | AO
RaFanSpd | Return Air Fan Speed | AV
RaFanSpdFbk | Return Air Fan Speed Feedback | AI
RaFanSpdFbk | Return Air Fan Speed Feedback | AV
RaFanSpdMax | Return Air Fan Maximum Speed | AV
RaFanSpdMin | Return Air Fan Minimum Speed | AV
RaFanSpdOfs | Return Air Fan Speed Offset | AV
RaFanStPrAlm | Return Air Fan Static Pressure Alarm | DI
RaFanStPrAlm | Return Air Fan Static Pressure Alarm | DV
RaFanStPrHalm | Return Air Fan High Static Pressure Alarm | DI
RaFanStPrHalm | Return Air Fan High Static Pressure Alarm | DV
RaFanStPrLalm | Return Air Fan Low Static Pressure Alarm | DI
RaFanStPrLalm | Return Air Fan Low Static Pressure Alarm | DV
RaFanSts | Return Air Fan Status | DI
RaFanSts | Return Air Fan Status | DV
RaFanStsHi | Return Air Fan High Speed Status | DI
RaFanStsHi | Return Air Fan High Speed Status | DV
RaFanStsLo | Return Air Fan Low Speed Status | DI
RaFanStsLo | Return Air Fan Low Speed Status | DV
RaFanStsMed | Return Air Fan Medium Speed Status | DI
RaFanStsMed | Return Air Fan Medium Speed Status | DV
RaFanSw | Return Air Fan Switch | DI
RaFanSw | Return Air Fan Switch | DV
RaFanTestSts | Return Air Fan Test Status | MV
RaFanVfdAlm | Return Air Fan Variable Frequency Drive Alarm | DI
RaFanVfdAlm | Return Air Fan Variable Frequency Drive Alarm | DV
RaFanVfdFlt | Return Air Fan Variable Frequency Drive Fault | DI
RaFanVfdFlt | Return Air Fan Variable Frequency Drive Fault | DV
RaFanVfdSts | Return Air Fan Variable Frequency Drive Status | DI
RaFanVfdSts | Return Air Fan Variable Frequency Drive Status | DV
RaFilDifPr | Return Air Filter Differential Pressure | AI
RaFilDifPr | Return Air Filter Differential Pressure | AV
RaFl | Return Air Flow | AI
RaFl | Return Air Flow | AV
RaFl | Return Air Flow | PNEU
RaFlFalm | Return Air Flow Fail Alarm | DV
RaFlFalmSv | Return Air Flow Fail Alarm Shunt Variable | DV
RaFlHlmt | Return Air Flow High Limit | AV
RaFlOfs | Return Air Flow Offset | AV
RaFlOfsSpt | Return Air Flow Offset Setpoint | AV
RaFlSpt | Return Air Flow Setpoint | AV
RaFlSptTestMd | Return Air Flow Setpoint Test Mode | MV
RaFlSptTestSts | Return Air Flow Setpoint Test Status | MV
RaFlTestSts | Return Air Flow Test Status | MV
RaHtgTmpSpt | Return Air Heating Temperature Setpoint | AV
RaIsoDprCmd | Return Air Isolation Damper Command | DO
RaIsoDprCmd | Return Air Isolation Damper Command | DV
RaIsoDprEswCls | Return Air Isolation Damper End Switch Closed | DI
RaIsoDprEswCls | Return Air Isolation Damper End Switch Closed | DV
RaIsoDprEswOpn | Return Air Isolation Damper End Switch Open | DI
RaIsoDprEswOpn | Return Air Isolation Damper End Switch Open | DV
RaNO2 | Return Air Nitrogen Dioxide | AI
RaNO2 | Return Air Nitrogen Dioxide | AV
RaNO2Dif | Return Air Nitrogen Dioxide Differential | AI
RaNO2Dif | Return Air Nitrogen Dioxide Differential | AV
RaNO2Spt | Return Air Nitrogen Dioxide Setpoint | AV
RaRh | Return Air Relative Humidity | AI
RaRh | Return Air Relative Humidity | AV
RaRhFalm | Return Air Relative Humidity Fail Alarm | DV
RaRhFalmSv | Return Air Relative Humidity Fail Alarm Shunt Variable | DV
RaRhSpt | Return Air Relative Humidity Setpoint | AV
RaSmkDet | Return Air Smoke Detector | DI
RaSmkDet | Return Air Smoke Detector | DV
RaStPr | Return Air Static Pressure | AI
RaStPr | Return Air Static Pressure | AV
RaStPrAlm | Return Air Static Pressure Alarm | DV
RaStPrFalm | Return Air Static Pressure Fail Alarm | DV
RaStPrFalmSv | Return Air Static Pressure Fail Alarm Shunt Variable | DV
RaStPrHalm | Return Air Static Pressure High Alarm | DI
RaStPrHalm | Return Air Static Pressure High Alarm | DV
RaStPrHlmtSw | Return Air Static High Pressure Limit Switch | DI
RaStPrHlmtSw | Return Air Static High Pressure Limit Switch | DV
RaStPrLalm | Return Air Low Static Pressure Alarm | DV
RaStPrLlmtSw | Return Air Static Low Pressure Limit Switch | DI
RaStPrLlmtSw | Return Air Static Low Pressure Limit Switch | DV
RaStPrSpt | Return Air Static Pressure Setpoint | AV
RaStPrSptMax | Return Air Static Pressure Maximum Setpoint | AV
RaStPrSptMin | Return Air Static Pressure Minimum Setpoint | AV
RaStPrSptTestSts | Return Air Static Pressure Setpoint Test Status | MV
RaStPrTestMd | Return Air Static Pressure Test Mode | MV
RaStPrTestSts | Return Air Static Pressure Test Status | MV
RatedBoxFlowFalm | Rated Box Flow Fail Alarm - Must Be Non-Zero | DV
RaTmp | Return Air Temperature | AI
RaTmp | Return Air Temperature | AV
RaTmpAlm | Return Air Temperature Alarm | DV
RaTmpAlmSv | Return Air Temperature Alarm Shunt Variable | DV
RaTmpAvg | Average Return Air Temperature | AV
RaTmpAvgCalc | Average Return Air Temperature Calculated | AV
RaTmpFalm | Return Air Temperature Fail Alarm | DV
RaTmpFalmSv | Return Air Temperature Fail Alarm Shunt Variable | DV
RaTmpHalm | Return Air Temperature High Alarm | DV
RaTmpHalmSv | Return Air Temperature High Alarm Shunt Variable | DV
RaTmpLalm | Return Air Temperature Low Alarm | DV
RaTmpLalmSv | Return Air Temperature Low Alarm Shunt Variable | DV
RaTmpSpt | Return Air Temperature Setpoint | AV
RaTmpSptClg | Return Air Temperature Cooling Setpoint | AV
RaTmpTestSts | Return Air Temperature Test Status | MV
RaVelPr | Return Air Velocity Pressure | AI
RaVelPr | Return Air Velocity Pressure | AV
RcirPFl | Recirculation Pump Flow | AI
RcirPFl | Recirculation Pump Flow | AV
RevVlvCmd | Reversing Valve Command | DO
RevVlvCmd | Reversing Valve Command | DV
RfgAlm | Refrigerant Alarm Indication | DI
RfgAlm | Refrigerant Alarm Indication | DV
RfgFl | Refrigerant Flow | AI
RfgFl | Refrigerant Flow | AV
RfgPr | Refrigerant Pressure | AI
RfgPr | Refrigerant Pressure | AV
RfgSclgDif | Refrigerant Subcooling Differential | AV
RfgSclgSpt | Refrigerant Subcooling Setpoint | AV
RfgShtgDif | Refrigerant Superheating Differential | AV
RhtCmd | Reheat Command | DO
RhtCmd | Reheat Command | DV
RhtCmdRt | Reheat Command Run Time | AV
RhtEnaDif | Reheat Enable Differential | AV
RhtEnaSpt | Reheat Enable Setpoint | AV
RhtLoad | Reheat Load | AV
RhtOnWu | Reheat on Warmup | DV
RhtPCmd | Reheat Pump Command | DO
RhtPCmd | Reheat Pump Command | DV
RhtPos | Reheat Position | AO
RhtPos | Reheat Position | AV
RhtPRt | Reheat Pump Run Time | AV
RhtPSts | Reheat Pump Status | DI
RhtPSts | Reheat Pump Status | DV
RhtRTmp | Reheat Return Water Temperature | AI
RhtRTmp | Reheat Return Water Temperature | AV
RhtSaTmp | Reheat Supply Air Temperature | AI
RhtSaTmp | Reheat Supply Air Temperature | AV
RhtSaTmpAvg | Reheat Supply Air Temperature Average | AV
RhtSel | Reheat Selector | MV
RhtStgNum | Number of Reheat Stages | AV
RhtTestMd | Reheat Test Mode | MV
RhtTestSts | Reheat Test Status | MV
RhtTmp | Reheat Temperature | AI
RhtTmp | Reheat Temperature | AV
RhtVlvCmd | Reheat Valve Command | DO
RhtVlvCmd | Reheat Valve Command | DV
RhtVlvCmdCls | Reheat Valve Close Command | DO
RhtVlvCmdCls | Reheat Valve Close Command | DV
RhtVlvCmdOpn | Reheat Valve Open Command | DO
RhtVlvCmdOpn | Reheat Valve Open Command | DV
RhtVlvDcr | Reheat Valve Decrease | DO
RhtVlvDcr | Reheat Valve Decrease | DV
RhtVlvFbk | Reheat Valve Feedback | AI
RhtVlvFbk | Reheat Valve Feedback | AV
RhtVlvInc | Reheat Valve Increase | DO
RhtVlvInc | Reheat Valve Increase | DV
RhtVlvLkAlm | Reheat Valve Leak Alarm | DV
RhtVlvLkAlmSv | Reheat Valve Leak Alarm Shunt Variable | DV
RhtVlvPos | Reheat Valve Position | AO
RhtVlvPos | Reheat Valve Position | AV
RlfDprCmd | Relief Damper Command | DO
RlfDprCmd | Relief Damper Command | DV
RlfDprCmdCls | Relief Damper Close Command | DO
RlfDprCmdCls | Relief Damper Close Command | DV
RlfDprCmdOpn | Relief Damper Open Command | DO
RlfDprCmdOpn | Relief Damper Open Command | DV
RlfDprFbk | Relief Air Damper Feedback | AI
RlfDprFbk | Relief Air Damper Feedback | AV
RlfDprPos | Relief Damper Position | AO
RlfDprPos | Relief Damper Position | AV
RlfDprPosMax | Relief Damper Position Maximum | AV
RlfDprPosMin | Relief Damper Position Minimum | AV
RlfDprTestMd | Relief Damper Test Mode | MV
RlfFanAmp | Relief Air Fan Amps | AI
RlfFanAmp | Relief Air Fan Amps | AV
RlfFanAmpFalm | Relief Fan Amp Fail Alarm | DV
RlfFanAryIsoDprCmd | Relief Air Fan Array Isolation Damper Command | DO
RlfFanAryIsoDprCmd | Relief Air Fan Array Isolation Damper Command | DV
RlfFanCmd | Relief Fan Command | DO
RlfFanCmd | Relief Fan Command | DV
RlfFanFbk | Relief Air Fan Feedback | AI
RlfFanFbk | Relief Air Fan Feedback | AV
RlfFanFl | Relief Air Fan Flow | AI
RlfFanFl | Relief Air Fan Flow | AV
RlfFanFof | Relief Fan Fail Off Alarm | DV
RlfFanFofSv | Relief Fan Fail Off Alarm Shunt Variable | DV
RlfFanFon | Relief Fan Fail On Alarm | DV
RlfFanFonSv | Relief Fan Fail On Alarm Shunt Variable | DV
RlfFanRt | Relief Fan Run Time | AV
RlfFanSpd | Relief Fan Speed | AO
RlfFanSpd | Relief Fan Speed | AV
RlfFanSpdMax | Relief Fan Maximum Speed | AV
RlfFanSpdMin | Relief Fan Minimum Speed | AV
RlfFanSts | Relief Fan Status | DI
RlfFanSts | Relief Fan Status | DV
RlfFanTestSts | Relief Fan Test Status | MV
RlfFanVfdAlm | Relief Air Fan Variable Frequency Drive Alarm | DI
RlfFanVfdAlm | Relief Air Fan Variable Frequency Drive Alarm | DV
RlfFanVfdSts | Relief Air Fan Variable Frequency Drive Status | DI
RlfFanVfdSts | Relief Air Fan Variable Frequency Drive Status | DV
RlfFl | Relief Air Flow | AI
RlfFl | Relief Air Flow | AV
RlfFl | Relief Air Flow | PNEU
RmCO | Room Carbon Monoxide | AI
RmCO | Room Carbon Monoxide | AV
RmCO2 | Room Carbon Dioxide | AI
RmCO2 | Room Carbon Dioxide | AV
RmCO2 | Room Carbon Dioxide | SS
RmCO2Avg | Average Room Carbon Dioxide | AV
RmCO2CalAlm | Room Carbon Dioxide Calibration Alarm | DV
RmCO2CalAlmSv | Room Carbon Dioxide Calibration Alarm Shunt Variable | DV
RmCO2Falm | Room Carbon Dioxide Fail Alarm | DV
RmCO2FalmSv | Room Carbon Dioxide Fail Alarm Shunt Variable | DV
RmCO2Halm | Room Carbon Dioxide High Alarm | DV
RmCO2HalmSpt | Room Carbon Dioxide High Alarm Setpoint | AV
RmCO2HalmSv | Room Carbon Dioxide High Alarm Shunt Variable | DV
RmCO2Hi | Highest Room Carbon Dioxide | AV
RmCO2HiHalm | Room Carbon Dioxide High-High Alarm | DV
RmCO2HiHalmSpt | Room Carbon Dioxide High-High Alarm Setpoint | AV
RmCO2HiWrn | Room Carbon Dioxide High Warning Alarm | DV
RmCO2HiWrnSpt | Room Carbon Dioxide High Warning Setpoint | AV
RmCO2Hlmt | Room Carbon Dioxide High Limit | AV
RmCO2Lalm | Room Carbon Dioxide Low Alarm | DV
RmCO2LalmSpt | Room Carbon Dioxide Low Alarm Setpoint | AV
RmCO2Llmt | Room Carbon Dioxide Low Limit | AV
RmCO2Lo | Lowest Room Carbon Dioxide | AV
RmCO2Load | Room Carbon Dioxide Load | AV
RmCO2LoLalm | Room Carbon Dioxide Low-Low Alarm | DV
RmCO2LoLalmSpt | Room Carbon Dioxide Low-Low Alarm Setpoint | AV
RmCO2LoWrn | Room Carbon Dioxide Low Warning Alarm | DV
RmCO2LoWrnSpt | Room Carbon Dioxide Low Warning Alarm Setpoint | AV
RmCO2Spt | Room Carbon Dioxide Setpoint | AV
RmCOHalm | Room Carbon Monoxide High Alarm | DV
RmCOHalmSpt | Room Carbon Monoxide High Alarm Setpoint | AV
RmCOHiHalm | Room Carbon Monoxide High-High Alarm | DV
RmCOHiHalmSpt | Room Carbon Monoxide High-High Alarm Setpoint | AV
RmCOHiWrn | Room Carbon Monoxide High Warning Alarm | DV
RmCOHiWrnSpt | Room Carbon Monoxide High Warning Setpoint | AV
RmCOHlmt | Room Carbon Monoxide High Limit | AV
RmCOLalm | Room Carbon Monoxide Low Alarm | DV
RmCOLalmSpt | Room Carbon Monoxide Low Alarm Setpoint | AV
RmCOLlmt | Room Carbon Monoxide Low Limit | AV
RmCOLoLalm | Room Carbon Monoxide Low-Low Alarm | DV
RmCOLoLalmSpt | Room Carbon Monoxide Low-Low Alarm Setpoint | AV
RmCOLoWrn | Room Carbon Monoxide Low Warning Alarm | DV
RmCOLoWrnSpt | Room Carbon Monoxide Low Warning Alarm Setpoint | AV
RmCOSpt | Room Carbon Monoxide Setpoint | AV
RmDehDif | Room Dehumidifier Differential | AV
RmDehRhSpt | Room Dehumidifier Relative Humidity Setpoint | AV
RmDehSptLlmt | Room Dehumidifier Setpoint Low Limit | AV
RmDew | Room Dew Point | AI
RmDew | Room Dew Point | AV
RmDewLoc | Room Dew Point Lockout | DV
RmDewLocDif | Room Dew Point Lockout Differential | AV
RmDifPr | Room Differential Pressure | AI
RmDifPr | Room Differential Pressure | AV
RmDifPrFalm | Room Differential Pressure Fail Alarm | DV
RmDifPrFalmSv | Room Differential Pressure Fail Alarm Shunt Variable | DV
RmDifPrHalm | Room Differential Pressure High Alarm | DV
RmDifPrHalmSv | Room Differential Pressure High Alarm Shunt Variable | DV
RmDifPrLalm | Room Differential Pressure Low Alarm | DV
RmDifPrLalmSv | Room Differential Pressure Low Alarm Shunt Variable | DV
RmDifPrLoad | Room Differential Pressure Load | AV
RmDifPrSpt | Room Differential Pressure Setpoint | AV
RmEnth | Room Enthalpy | AI
RmEnth | Room Enthalpy | AV
RmLux | Room Illuminance | AI
RmLux | Room Illuminance | AV
RmLuxMax | Maximum Room Illuminance | AV
RmNO2 | Room Nitrogen Dioxide | AI
RmNO2 | Room Nitrogen Dioxide | AV
RmNO2Halm | Room Nitrogen Dioxide Level High Alarm | DV
RmNO2HalmSpt | Room Nitrogen Dioxide Level High Alarm Setpoint | AV
RmNO2HiHalm | Room Nitrogen Dioxide Level High-High Alarm | DV
RmNO2HiHalmSpt | Room Nitrogen Dioxide Level High-High Alarm Setpoint | AV
RmNO2HiWrn | Room Nitrogen Dioxide Level High Warning Alarm | DV
RmNO2HiWrnSpt | Room Nitrogen Dioxide Level High Warning Setpoint | AV
RmNO2Hlmt | Room Nitrogen Dioxide Level High Limit | AV
RmNO2Lalm | Room Nitrogen Dioxide Level Low Alarm | DV
RmNO2LalmSpt | Room Nitrogen Dioxide Level Low Alarm Setpoint | AV
RmNO2Llmt | Room Nitrogen Dioxide Level Low Limit | AV
RmNO2LoLalm | Room Nitrogen Dioxide Level Low-Low Alarm | DV
RmNO2LoLalmSpt | Room Nitrogen Dioxide Level Low-Low Alarm Setpoint | AV
RmNO2LoWrn | Room Nitrogen Dioxide Level Low Warning Alarm | DV
RmNO2LoWrnSpt | Room Nitrogen Dioxide Level Low Warning Alarm Setpoint | AV
RmNO2Spt | Room Nitrogen Dioxide Setpoint | AV
RmO2 | Room Oxygen | AI
RmO2 | Room Oxygen | AV
RmOccOvr | Room Occupancy Override | DI
RmOccOvr | Room Occupancy Override | DV
RmOccOvr | Room Occupancy Override | SS
RmRh | Room Relative Humidity | AI
RmRh | Room Relative Humidity | AV
RmRh | Room Relative Humidity | SS
RmRhAvg | Average Room Relative Humidity | AV
RmRhEna | Room Relative Humidity Enable | DV
RmRhFalm | Room Relative Humidity Fail Alarm | DV
RmRhFalmSv | Room Relative Humidity Fail Alarm Shunt Variable | DV
RmRhHalm | Room Relative Humidity High Alarm | DV
RmRhHalmSv | Room Relative Humidity High Alarm Shunt Variable | DV
RmRhHi | Highest Room Relative Humidity | AV
RmRhHlmt | Room Relative Humidity High Limit | AV
RmRhLalm | Room Relative Humidity Low Alarm | DV
RmRhLalmSv | Room Relative Humidity Low Alarm Shunt Variable | DV
RmRhLo | Lowest Room Relative Humidity | AV
RmRhOfs | Room Relative Humidity Offset | AV
RmRhSel | Room Relative Humidity Display Selector | MV
RmRhSpt | Room Relative Humidity Setpoint | AV
RmRhSptBs | Room Relative Humidity Base Setpoint | AV
RmRhSptHlmt | Room Relative Humidity Setpoint High Limit | AV
RmStPr | Room Static Pressure | AI
RmStPr | Room Static Pressure | AV
RmStPrSpt | Room Static Pressure Setpoint | AV
RmTmp | Room Temperature | AI
RmTmp | Room Temperature | AV
RmTmp | Room Temperature | SS
RmTmpAlmSv | Room Temperature Alarm Shunt Variable | DV
RmTmpAvg | Average Room Temperature | AV
RmTmpFalm | Room Temperature Fail Alarm | DV
RmTmpFalmSv | Room Temperature Fail Alarm Shunt Variable | DV
RmTmpFzSbAlm | Room Temperature Freeze Setback Alarm | DV
RmTmpFzSbAlmSv | Room Temperature Freeze Setback Alarm Shunt Variable | DV
RmTmpFzSbMd | Room Temperature Freeze Setback Mode | DV
RmTmpFzSbReq | Room Temperature Freeze Setback Request | DV
RmTmpHalm | Room Temperature High Alarm | DV
RmTmpHalmSv | Room Temperature High Alarm Shunt Variable | DV
RmTmpHi | Highest Room Temperature | AV
RmTmpHiWrn | Room Temperature High Warning | DV
RmTmpHiWrnSv | Room Temperature High Warning Shunt Variable | DV
RmTmpLalm | Room Temperature Low Alarm | DV
RmTmpLalmSv | Room Temperature Low Alarm Shunt Variable | DV
RmTmpLo | Lowest Room Temperature | AV
RmTmpLoWrn | Room Temperature Low Warning | DV
RmTmpLoWrnSv | Room Temperature Low Warning Shunt Variable | DV
RmTmpSbReq | Room Temperature Setback Request | DV
RmTmpSpt | Room Temperature Setpoint | AV
RmTmpSptAdj | Room Temperature Setpoint Adjustment | AI
RmTmpSptAdj | Room Temperature Setpoint Adjustment | AV
RmTmpSptAdj | Room Temperature Setpoint Adjustment | SS
RmTmpSptAdjRng | Room Temperature Setpoint Adjustment Range | AV
RmTmpSptAvg | Room Temperature Average Setpoint | AV
RmTmpSptClg | Room Temperature Cooling Setpoint | AV
RmTmpSptClgMax | Room Temperature Maximum Cooling Setpoint | AV
RmTmpSptClgMin | Room Temperature Minimum Cooling Setpoint | AV
RmTmpSptDif | Room Temperature Setpoint Differential | AV
RmTmpSptDifLlmt | Room Temperature Setpoint Differential Low Limit | AV
RmTmpSptEff | Room Temperature Effective Setpoint | AV
RmTmpSptHtg | Room Temperature Heating Setpoint | AV
RmTmpSptHtgMax | Room Temperature Maximum Heating Setpoint | AV
RmTmpSptHtgMin | Room Temperature Minimum Heating Setpoint | AV
RmTmpSptSb | Room Temperature Setback Setpoint | AV
RmTmpSptSbDif | Room Temperature Setback Differential | AV
RmTmpSptStbOfs | Room Temperature Setpoint Standby Offset | AV
RmTmpSptSu | Room Temperature Setup Setpoint | AV
RmTmpSptSuDif | Room Temperature Setup Differential | AV
RmTmpSuReq | Room Temperature Setup Request | DV
RmTmpTestSts | Room Temperature Test Status | MV
RmtRmTmp | Remote Room Temperature | AI
RmtRmTmp | Remote Room Temperature | AV
RmtRmTmp | Remote Room Temperature | SS
RmVntLoad | Room Ventilation Load | AV
RmVoc | Room Volatile Organic Compounds | AI
RmVoc | Room Volatile Organic Compounds | AV
RmVoc | Room Volatile Organic Compounds | SS
RotLdTs | Rotate Lead Time Schedule | DV
RotSw | Rotate Switch | DV
RpHwVlvPos | Radiant Panel Hot Water Valve Position | AO
RpHwVlvPos | Radiant Panel Hot Water Valve Position | AV
RstCycActv | Floating Actuator Reset Cycle Active | DV
RstReqCyc | Reset Request Hour Cycle Time | AV
RstReqHlmt | Reset Request Hour High Limit Setpoint | AV
RtuEna | Rooftop Unit Enable | DV
SaBalBoxFl | Supply Air Balanced Box Rated Flow | AV
SaBalFlCorFct | Supply Air Balanced Box Flow Correction Factor | AV
SaBalKFct | Supply Air Balanced k-Factor | AV
SaBoxFlMax | Supply Air Maximum Measured Box Flow | AV
SaBoxFlMid | Supply Air Medium Measured Box Flow | AV
SaBoxFlMin | Supply Air Minimum Measured Box Flow | AV
SaClsofTestSts | Supply Air Close Off Test Status | MV
SaCO | Supply Air Carbon Monoxide | AI
SaCO | Supply Air Carbon Monoxide | AV
SaCO2 | Supply Air Carbon Dioxide | AI
SaCO2 | Supply Air Carbon Dioxide | AV
SaCO2Spt | Supply Air Carbon Dioxide Setpoint | AV
SaCOSpt | Supply Air Carbon Monoxide Setpoint | AV
SaDew | Supply Air Dew Point | AI
SaDew | Supply Air Dew Point | AV
SaDewHlmt | Supply Air Dew Point High Limit | AV
SaDifPr | Supply Air Differential Pressure | AI
SaDifPr | Supply Air Differential Pressure | AV
SaDprCmd | Supply Air Damper Command | DO
SaDprCmd | Supply Air Damper Command | DV
SaDprCmdCls | Supply Air Damper Close Command | DO
SaDprCmdCls | Supply Air Damper Close Command | DV
SaDprCmdOpn | Supply Air Damper Open Command | DO
SaDprCmdOpn | Supply Air Damper Open Command | DV
SaDprFbk | Supply Air Damper Feedback | AI
SaDprFbk | Supply Air Damper Feedback | AV
SaDprLkAlm | Supply Air Damper Leak Alarm | DV
SaDprLkAlmSv | Supply Air Damper Leak Alarm Shunt Variable | DV
SaDprPos | Supply Air Damper Position | AO
SaDprPos | Supply Air Damper Position | AV
SaDprTestMd | Supply Air Damper Test Mode | MV
SaEaFlDif | Supply Air Exhaust Air Flow Differential | AV
SaEnth | Supply Air Enthalpy | AI
SaEnth | Supply Air Enthalpy | AV
SaEnthSpt | Supply Air Enthalpy Setpoint | AV
SaFanAlm | Supply Air Fan Alarm | DI
SaFanAlm | Supply Air Fan Alarm | DV
SaFanAmp | Supply Air Fan Amps | AI
SaFanAmp | Supply Air Fan Amps | AV
SaFanAmpFalm | Supply Air Fan Amp Fail Alarm | DV
SaFanAryIsoDprCmd | Supply Air Fan Array Isolation Damper Command | DO
SaFanAryIsoDprCmd | Supply Air Fan Array Isolation Damper Command | DV
SaFanCmd | Supply Air Fan Command | DO
SaFanCmd | Supply Air Fan Command | DV
SaFanCmdHi | Supply Air Fan High Speed Command | DO
SaFanCmdHi | Supply Air Fan High Speed Command | DV
SaFanCmdLo | Supply Air Fan Low Speed Command | DO
SaFanCmdLo | Supply Air Fan Low Speed Command | DV
SaFanCmdMed | Supply Air Fan Medium Speed Command | DO
SaFanCmdMed | Supply Air Fan Medium Speed Command | DV
SaFanDifPr | Supply Air Fan Differential Pressure | AI
SaFanDifPr | Supply Air Fan Differential Pressure | AV
SaFanDof | Supply Air Fan Delay Off | AV
SaFanDon | Supply Air Fan Delay On | AV
SaFanDprCmd | Supply Air Fan Damper Command | DO
SaFanDprCmd | Supply Air Fan Damper Command | DV
SaFanDprCmdCls | Supply Air Fan Damper Close Command | DO
SaFanDprCmdCls | Supply Air Fan Damper Close Command | DV
SaFanDprCmdOpn | Supply Air Fan Damper Open Command | DO
SaFanDprCmdOpn | Supply Air Fan Damper Open Command | DV
SaFanFbk | Supply Air Fan Feedback | AI
SaFanFbk | Supply Air Fan Feedback | AV
SaFanFl | Supply Air Fan Flow | AI
SaFanFl | Supply Air Fan Flow | AV
SaFanFlTot | Supply Air Fan Flow Total | AV
SaFanFof | Supply Air Fan Fail Off Alarm | DV
SaFanFofSv | Supply Air Fan Fail Off Alarm Shunt Variable | DV
SaFanFon | Supply Air Fan Fail On Alarm | DV
SaFanFonSv | Supply Air Fan Fail On Alarm Shunt Variable | DV
SaFanFreq | Supply Air Fan Frequency | AO
SaFanFreq | Supply Air Fan Frequency | AV
SaFanKw | Supply Air Fan Kilowatts | AV
SaFanKwh | Supply Air Fan Kilowatt-Hours | AV
SaFanMd | Supply Air Fan Mode | MV
SaFanRt | Supply Air Fan Run Time | AV
SaFanSaStPr | Supply Air Fan Supply Air Static Pressure | AI
SaFanSaStPr | Supply Air Fan Supply Air Static Pressure | AV
SaFanSpd | Supply Air Fan Speed | AO
SaFanSpd | Supply Air Fan Speed | AV
SaFanSpdDbd | Supply Air Fan Deadband Speed | AV
SaFanSpdFbk | Supply Air Fan Speed Feedback | AI
SaFanSpdFbk | Supply Air Fan Speed Feedback | AV
SaFanSpdMax | Supply Air Fan Maximum Speed | AV
SaFanSpdMaxClg | Supply Air Fan Cooling Maximum Speed | AV
SaFanSpdMaxHtg | Supply Air Fan Heating Maximum Speed | AV
SaFanSpdMedClg | Supply Air Fan Cooling Medium Speed | AV
SaFanSpdMin | Supply Air Fan Minimum Speed | AV
SaFanSpdMinClg | Supply Air Fan Cooling Minimum Speed | AV
SaFanSpdMinHtg | Supply Air Fan Heating Minimum Speed | AV
SaFanSpdSpt | Supply Air Fan Speed Setpoint | AV
SaFanStPrAlm | Supply Air Fan Static Pressure Alarm | DI
SaFanStPrAlm | Supply Air Fan Static Pressure Alarm | DV
SaFanSts | Supply Air Fan Status | DI
SaFanSts | Supply Air Fan Status | DV
SaFanStsAmpSptOf | Supply Air Fan Status Amp Off Setpoint | AV
SaFanStsAmpSptOn | Supply Air Fan Status Amp On Setpoint | AV
SaFanStsHi | Supply Air Fan High Speed Status | DI
SaFanStsHi | Supply Air Fan High Speed Status | DV
SaFanStsLo | Supply Air Fan Low Speed Status | DI
SaFanStsLo | Supply Air Fan Low Speed Status | DV
SaFanStsMed | Supply Air Fan Medium Speed Status | DI
SaFanStsMed | Supply Air Fan Medium Speed Status | DV
SaFanSw | Supply Air Fan Switch | DI
SaFanSw | Supply Air Fan Switch | DV
SaFanTestSts | Supply Air Fan Test Status | MV
SaFanVfdAlm | Supply Air Fan Variable Frequency Drive Alarm | DI
SaFanVfdAlm | Supply Air Fan Variable Frequency Drive Alarm | DV
SaFanVfdFlt | Supply Air Fan Variable Frequency Drive Fault | DI
SaFanVfdFlt | Supply Air Fan Variable Frequency Drive Fault | DV
SaFanVfdSts | Supply Air Fan Variable Frequency Drive Status | DI
SaFanVfdSts | Supply Air Fan Variable Frequency Drive Status | DV
SaFilAlm | Supply Air Filter Alarm | DI
SaFilAlm | Supply Air Filter Alarm | DV
SaFilAlmSv | Supply Air Filter Alarm Shunt Variable | DV
SaFilDifPr | Supply Air Filter Differential Pressure | AI
SaFilDifPr | Supply Air Filter Differential Pressure | AV
SaFilDifPrHlmt | Supply Air Filter Differential Pressure High Limit | AV
SaFilSts | Supply Air Filter Status | DI
SaFilSts | Supply Air Filter Status | DV
SaFl | Supply Air Flow | AI
SaFl | Supply Air Flow | AV
SaFl | Supply Air Flow | PNEU
SaFlBalMd | Supply Air Flow Balance Mode | MV
SaFlCalAlm | Supply Air Flow Calibration Alarm | DV
SaFlCalAlmSv | Supply Air Flow Calibration Alarm Shunt Variable | DV
SaFlLalm | Supply Air Flow Low Alarm | DV
SaFlLalmSv | Supply Air Flow Low Alarm Shunt Variable | DV
SaFlLoWrn | Supply Air Flow Low Warning | DV
SaFlLoWrnSv | Supply Air Flow Low Warning Shunt Variable | DV
SaFlMaxTestSts | Maximum Supply Air Flow Test Status | MV
SaFlMinTestSts | Minimum Supply Air Flow Test Status | MV
SaFlSpt | Supply Air Flow Setpoint | AV
SaFlSptClgMax | Maximum Cooling Supply Air Flow Setpoint | AV
SaFlSptClgMid | Intermediate Cooling Supply Air Flow Setpoint | AV
SaFlSptClgMin | Minimum Cooling Supply Air Flow Setpoint | AV
SaFlSptHtgMax | Maximum Heating Supply Air Flow Setpoint | AV
SaFlSptHtgMid | Intermediate Heating Supply Air Flow Setpoint | AV
SaFlSptHtgMin | Minimum Heating Supply Air Flow Setpoint | AV
SaFlSptMax | Maximum Supply Air Flow Setpoint | AV
SaFlSptMin | Minimum Supply Air Flow Setpoint | AV
SaFlSptOfs | Supply Air Flow Setpoint Offset | AV
SaFlTestMd | Supply Air Flow Test Mode | MV
SaFlTestSts | Supply Air Flow Test Status | MV
SaHoodFlMax | Supply Air Maximum Measured Hood Flow | AV
SaHoodFlMid | Supply Air Intermediate Measured Hood Flow | AV
SaHoodFlMin | Supply Air Minimum Measured Hood Flow | AV
SaIsoDprCmd | Supply Air Isolation Damper Command | DO
SaIsoDprCmd | Supply Air Isolation Damper Command | DV
SaIsoDprEswCls | Supply Air Isolation Damper End Switch Closed | DI
SaIsoDprEswCls | Supply Air Isolation Damper End Switch Closed | DV
SaIsoDprEswOpn | Supply Air Isolation Damper End Switch Open | DI
SaIsoDprEswOpn | Supply Air Isolation Damper End Switch Open | DV
SaNO2 | Supply Air Nitrogen Dioxide | AI
SaNO2 | Supply Air Nitrogen Dioxide | AV
SaNO2Spt | Supply Air Nitrogen Dioxide Setpoint | AV
SaPhtTmpFalm | Preheat Temperature Fail Alarm | DV
SaPhtTmpHalm | Preheat Temperature High Alarm | DV
SaPhtTmpLalm | Preheat Temperature Low Alarm | DV
SaRatedBoxFlow | Supply Air Box Rated Flow | AV
SaRatedBoxFlowFalm | Supply Air Rated Box Flow Fail Alarm - Must Be Non-Zero | DV
SaRh | Supply Air Relative Humidity | AI
SaRh | Supply Air Relative Humidity | AV
SaRhFalm | Supply Air Relative Humidity Fail Alarm | DV
SaRhHalm | Supply Air Relative Humidity High Alarm | DV
SaRhHlmtSpt | Supply Air Relative Humidity High Limit Setpoint | AV
SaRhLalm | Supply Air Relative Humidity Low Alarm | DV
SaRhSpt | Supply Air Relative Humidity Setpoint | AV
SashPos | Sash Position | AI
SashPos | Sash Position | AV
SaSmkDet | Supply Air Smoke Detector | DI
SaSmkDet | Supply Air Smoke Detector | DV
SaSmkDetAlm | Supply Air Smoke Detector Alarm | DI
SaSmkDetAlm | Supply Air Smoke Detector Alarm | DV
SaStPr | Supply Air Static Pressure | AI
SaStPr | Supply Air Static Pressure | AV
SaStPrAlm | Supply Air Static Pressure Alarm | DV
SaStPrAvg | Average Supply Air Static Pressure | AV
SaStPrAvgCalc | Average Supply Air Static Pressure Calculated | AV
SaStPrFalm | Supply Air Static Pressure Fail Alarm | DV
SaStPrFalmSv | Supply Air Static Pressure Fail Alarm Shunt Variable | DV
SaStPrHalm | Supply Air High Static Pressure Alarm | DV
SaStPrHlmtSw | Supply Air Static High Pressure Limit Switch | DI
SaStPrHlmtSw | Supply Air Static High Pressure Limit Switch | DV
SaStPrLalm | Supply Air Low Static Pressure Alarm | DV
SaStPrLlmtSw | Supply Air Static Low Pressure Limit Switch | DI
SaStPrLlmtSw | Supply Air Static Low Pressure Limit Switch | DV
SaStPrSpt | Supply Air Static Pressure Setpoint | AV
SaStPrSptMax | Supply Air Static Pressure Maximum Setpoint | AV
SaStPrSptMin | Supply Air Static Pressure Minimum Setpoint | AV
SaStPrSptRstIgnReq | Supply Air Static Pressure Setpoint Reset Ignored Requests | AV
SaStPrSptRstReq | Supply Air Static Pressure Setpoint Reset Requests | AV
SaStPrSptTestSts | Supply Air Static Pressure Setpoint Test Status | MV
SaStPrTestMd | Supply Air Static Pressure Test Mode | MV
SaStPrTestSts | Supply Air Static Pressure Test Status | MV
SaTmp | Supply Air Temperature | AI
SaTmp | Supply Air Temperature | AV
SaTmpAvg | Average Supply Air Temperature | AV
SaTmpAvgCalc | Average Supply Air Temperature Calculated | AV
SaTmpFalm | Supply Air Temperature Fail Alarm | DV
SaTmpFalmSv | Supply Air Temperature Fail Alarm Shunt Variable | DV
SaTmpHalm | Supply Air Temperature High Alarm | DV
SaTmpHalmSv | Supply Air Temperature High Alarm Shunt Variable | DV
SaTmpHlmt | Supply Air Temperature Setpoint High Limit | AV
SaTmpHlmtDif | Supply Air Temperature High Limit Differential | AV
SaTmpLalm | Supply Air Temperature Low Alarm | DV
SaTmpLalmSv | Supply Air Temperature Low Alarm Shunt Variable | DV
SaTmpLlmt | Supply Air Temperature Low Limit | AV
SaTmpLoWrn | Supply Air Temperature Low Warning | DV
SaTmpLoWrnSv | Supply Air Temperature Low Warning Shunt Variable | DV
SaTmpRstClgReq | Supply Air Temperature Reset Cooling Requests | AV
SaTmpSpt | Supply Air Temperature Setpoint | AV
SaTmpSptClg | Supply Air Cooling Setpoint | AV
SaTmpSptClgMax | Maximum Supply Air Temperature Cooling Setpoint | AV
SaTmpSptClgMin | Minimum Supply Air Temperature Cooling Setpoint | AV
SaTmpSptClgTestSts | Supply Air Temperature Cooling Setpoint Test Status | MV
SaTmpSptEcon | Supply Air Temperature Economizer Setpoint | AV
SaTmpSptHtg | Supply Air Temperature Heating Setpoint | AV
SaTmpSptHtgMax | Maximum Supply Air Temperature Heating Setpoint | AV
SaTmpSptHtgMin | Minimum Supply Air Temperature Heating Setpoint | AV
SaTmpSptHtgTestSts | Supply Air Temperature Heating Setpoint Test Status | MV
SaTmpSptMax | Supply Air Temperature Maximum Setpoint | AV
SaTmpSptMin | Supply Air Temperature Minimum Setpoint | AV
SaTmpSptOaTmpMax | Supply Air Temperature Setpoint Outside Air Temperature Maximum | AV
SaTmpSptOaTmpMin | Supply Air Temperature Setpoint Outside Air Temperature Minimum | AV
SaTmpSptRstIgnReq | Supply Air Temperature Setpoint Reset Ignored Requests | AV
SaTmpSptRstReq | Supply Air Temperature Setpoint Reset Requests | AV
SaTmpSptUnoc | Supply Air Unoccupied Temperature Setpoint | AV
SaTmpSptWu | Supply Air Temperature Warmup Setpoint | AV
SaTmpTestMd | Supply Air Temperature Test Mode | MV
SaTmpTestSts | Supply Air Temperature Test Status | MV
SaUvLtAlm | Supply Air Ultraviolet Light Alarm | DI
SaUvLtAlm | Supply Air Ultraviolet Light Alarm | DV
SaUvLtCmd | Supply Air Ultraviolet Light Command | DO
SaUvLtCmd | Supply Air Ultraviolet Light Command | DV
SaUvLtFlt | Supply Air Ultraviolet Light Fault | DI
SaUvLtFlt | Supply Air Ultraviolet Light Fault | DV
SaUvLtFof | Supply Air Ultraviolet Light Fail Off Alarm | DV
SaUvLtFon | Supply Air Ultraviolet Light Fail On Alarm | DV
SaUvLtRt | Supply Air Ultraviolet Light Run Time | AV
SaUvLtSts | Supply Air Ultraviolet Light Status | DI
SaUvLtSts | Supply Air Ultraviolet Light Status | DV
SaVelPr | Supply Air Velocity Pressure | AI
SaVelPr | Supply Air Velocity Pressure | AV
SaVelPrSpt | Supply Air Velocity Pressure Setpoint | AV
SaVelPrTestSts | Supply Air Velocity Pressure Test Status | MV
SchwDifPr | Secondary Chilled Water Differential Pressure | AI
SchwDifPr | Secondary Chilled Water Differential Pressure | AV
SchwDifPrSpt | Secondary Chilled Water Differential Pressure Setpoint | AV
SchwDifPrVlvPos | Secondary Chilled Water Differential Pressure Valve Position | AO
SchwDifPrVlvPos | Secondary Chilled Water Differential Pressure Valve Position | AV
SchwFl | Secondary Chilled Water Flow | AI
SchwFl | Secondary Chilled Water Flow | AV
SchwFlCalAlm | Secondary Chilled Water Flow Calibration Alarm | DI
SchwFlCalAlm | Secondary Chilled Water Flow Calibration Alarm | DV
SchwFlSpt | Secondary Chilled Water Flow Setpoint | AV
SchwPAlm | Secondary Chilled Water Pump Alarm | DI
SchwPAlm | Secondary Chilled Water Pump Alarm | DV
SchwPAmp | Secondary Chilled Water Pump Amps | AI
SchwPAmp | Secondary Chilled Water Pump Amps | AV
SchwPCmd | Secondary Chilled Water Pump Command | DO
SchwPCmd | Secondary Chilled Water Pump Command | DV
SchwPCmdDof | Secondary Chilled Water Pump Command Delay Off | AV
SchwPCmdDon | Secondary Chilled Water Pump Command Delay On | AV
SchwPCmdOvrAlm | Secondary Chilled Water Pump Command Forced By Operator Alarm | DV
SchwPDifPr | Secondary Chilled Water Pump Differential Pressure | AI
SchwPDifPr | Secondary Chilled Water Pump Differential Pressure | AV
SchwPDifPrSpt | Secondary Chilled Water Pump Differential Pressure Setpoint | AV
SchwPEna | Secondary Chilled Water Pump Enable | DV
SchwPEnaDof | Secondary Chilled Water Pump Enable Delay Off | AV
SchwPEnaDon | Secondary Chilled Water Pump Enable Delay On | AV
SchwPFbk | Secondary Chilled Water Pump Feedback | AI
SchwPFbk | Secondary Chilled Water Pump Feedback | AV
SchwPFl | Secondary Chilled Water Pump Flow | AI
SchwPFl | Secondary Chilled Water Pump Flow | AV
SchwPFof | Secondary Chilled Water Pump Fail Off Alarm | DV
SchwPFon | Secondary Chilled Water Pump Fail On Alarm | DV
SchwPFreq | Secondary Chilled Water Pump Frequency | AO
SchwPFreq | Secondary Chilled Water Pump Frequency | AV
SchwPKw | Secondary Chilled Water Pump Kilowatts | AI
SchwPKw | Secondary Chilled Water Pump Kilowatts | AV
SchwPKwh | Secondary Chilled Water Pump Kilowatt-Hours | AV
SchwPKwMax | Secondary Chilled Water Pump Kilowatt Maximum | AV
SchwPKwTot | Secondary Chilled Water Pump Kilowatts Total | AV
SchwPLclLoc | Secondary Chilled Water Pump Local Lockout | DV
SchwPLclLocRst | Secondary Chilled Water Pump Local Lockout Reset | DV
SchwPLd | Secondary Chilled Water Pump Lead | AV
SchwPLdMan | Secondary Chilled Water Pump Lead Manual | AV
SchwPLdRotTs | Secondary Chilled Water Pump Lead Rotation Schedule | AV
SchwPLg | Secondary Chilled Water Pump Lag | AV
SchwPLgDof | Secondary Chilled Water Pump Lag Delay Off | AV
SchwPLgDon | Secondary Chilled Water Pump Lag Delay On | AV
SchwPLgMan | Secondary Chilled Water Pump Lag Manual | AV
SchwPMaintMd | Secondary Chilled Water Pump Maintenance Mode | DV
SchwPMaintMdAlm | Secondary Chilled Water Pump Maintenance Mode Alarm | DV
SchwPMaintReqAlm | Secondary Chilled Water Pump Maintenance Request Alarm | DV
SchwPMaintReqRtRst | Secondary Chilled Water Pump Maintenance Request Run Time Reset | DV
SchwPNumAvl | Number of Secondary Chilled Water Pumps Available | AV
SchwPNumLclLoc | Number of Secondary Chilled Water Pumps In Local Lockout | AV
SchwPNumOvrOn | Number of Secondary Chilled Water Pumps Which Are Overridden On | AV
SchwPNumReq | Number of Secondary Chilled Water Pumps Request | AV
SchwPNumRun | Number of Secondary Chilled Water Pumps Running | AV
SchwPOvrOn | Secondary Chilled Water Pump Overridden On | DV
SchwPRotCmdTs | Secondary Chilled Water Pump Rotation Command From Time Schedule | DV
SchwPRotLdMan | Secondary Chilled Water Pump Manual Lead Rotation | DV
SchwPRotLdMd | Secondary Chilled Water Pump Lead Rotation Mode | MV
SchwPRotOrdManValid | Secondary Chilled Water Pump Manual Rotation Order Valid | DV
SchwPRotOrdValid | Secondary Chilled Water Pump Rotation Order Valid | DV
SchwPRotSel | Secondary Chilled Water Pump Rotation Mode Select | MV
SchwPRotSelfCor | Secondary Chilled Water Pump Rotation Self Correcting Option | DV
SchwPRotSw | Secondary Chilled Water Pump Rotation Switch | DV
SchwPRotTsFrcRot | Secondary Chilled Water Rotation Time Schedule Force Rotation Option | DV
SchwPRotTsRot | Secondary Chilled Water Pump Rotation Time Schedule Force Rotation Option | DV
SchwPRt | Secondary Chilled Water Pump Run Time | AV
SchwPRtRst | Secondary Chilled Water Pump Run Time Reset | DV
SchwPSpd | Secondary Chilled Water Pump Speed | AO
SchwPSpd | Secondary Chilled Water Pump Speed | AV
SchwPSpdFbk | Secondary Chilled Water Pump Speed Feedback | AI
SchwPSpdFbk | Secondary Chilled Water Pump Speed Feedback | AV
SchwPSpdHlmt | Secondary Chilled Water Pump Speed High Limit | AV
SchwPSpdLlmt | Secondary Chilled Water Pump Speed Low Limit | AV
SchwPSpdMin | Secondary Chilled Water Pump Speed Minimum | AV
SchwPSpdOvrAlm | Secondary Chilled Water Pump Speed Forced By Operator Alarm | DV
SchwPSpdStrt | Secondary Chilled Water Pump Startup Speed | AV
SchwPStrtTm | Secondary Chilled Water Pump Startup Time | AV
SchwPSts | Secondary Chilled Water Pump Status | DI
SchwPSts | Secondary Chilled Water Pump Status | DV
SchwPStsOvrAlm | Secondary Chilled Water Pump Status Forced By Operator Alarm | DV
SchwPVfdAlm | Secondary Chilled Water Pump Variable Frequency Drive Alarm | DI
SchwPVfdAlm | Secondary Chilled Water Pump Variable Frequency Drive Alarm | DV
SchwPXrt | Secondary Chilled Water Pump Extended Run Time | AV
SchwRFlCalAlm | Secondary Chilled Water Return Flow Calibration Alarm | DI
SchwRFlCalAlm | Secondary Chilled Water Return Flow Calibration Alarm | DV
SchwRPr | Secondary Chilled Water Return Pressure | AI
SchwRPr | Secondary Chilled Water Return Pressure | AV
SchwRTmp | Secondary Chilled Water Return Temperature | AI
SchwRTmp | Secondary Chilled Water Return Temperature | AV
SchwRTmpSpt | Secondary Chilled Water Return Temperature Setpoint | AV
SchwSFl | Secondary Chilled Water Supply Flow | AI
SchwSFl | Secondary Chilled Water Supply Flow | AV
SchwSFlCalAlm | Secondary Chilled Water Supply Flow Calibration Alarm | DI
SchwSFlCalAlm | Secondary Chilled Water Supply Flow Calibration Alarm | DV
SchwSPr | Secondary Chilled Water Supply Pressure | AI
SchwSPr | Secondary Chilled Water Supply Pressure | AV
SchwSTmp | Secondary Chilled Water Supply Temperature | AI
SchwSTmp | Secondary Chilled Water Supply Temperature | AV
SchwSTmpAlm | Secondary Chilled Water Supply Temperature Alarm | DV
SchwSTmpSpt | Secondary Chilled Water Supply Temperature Setpoint | AV
SecAlm | Security Alarm | DV
SelfTestMd | Self Test Mode | MV
SelfTestMdAlm | Self Test Mode Alarm | DV
SelfTestMdAlmSv | Self Test Mode Alarm Shunt Variable | DV
ShwDifPr | Secondary Hot Water Differential Pressure | AI
ShwDifPr | Secondary Hot Water Differential Pressure | AV
ShwDifPrSpt | Secondary Hot Water Differential Pressure Setpoint | AV
ShwDifPrVlvPos | Secondary Hot Water Differential Pressure Valve Position | AO
ShwDifPrVlvPos | Secondary Hot Water Differential Pressure Valve Position | AV
ShwFl | Secondary Hot Water Flow | AI
ShwFl | Secondary Hot Water Flow | AV
ShwFlAlm | Secondary Hot Water Flow Alarm | DI
ShwFlAlm | Secondary Hot Water Flow Alarm | DV
ShwFlCalAlm | Secondary Hot Water Flow Calibration Alarm | DI
ShwFlCalAlm | Secondary Hot Water Flow Calibration Alarm | DV
ShwMixTmp | Secondary Hot Water Mixed Temperature | AI
ShwMixTmp | Secondary Hot Water Mixed Temperature | AV
ShwMixTmpSpt | Secondary Hot Water Mixed Temperature Setpoint | AV
ShwMixVlvPos | Secondary Hot Water Mixing Valve Position | AO
ShwMixVlvPos | Secondary Hot Water Mixing Valve Position | AV
ShwPAmp | Secondary Hot Water Pump Amps | AI
ShwPAmp | Secondary Hot Water Pump Amps | AV
ShwPCmd | Secondary Hot Water Pump Command | DO
ShwPCmd | Secondary Hot Water Pump Command | DV
ShwPDifPr | Secondary Hot Water pump Differential Pressure | AI
ShwPDifPr | Secondary Hot Water pump Differential Pressure | AV
ShwPDifPrSpt | Secondary Hot Water Pump Differential Pressure Setpoint | AV
ShwPEna | Secondary Hot Water Pump Enable | DV
ShwPFbk | Secondary Hot Water Pump VFD Feedback | AI
ShwPFbk | Secondary Hot Water Pump VFD Feedback | AV
ShwPFof | Secondary Hot Water Pump Fail Off Alarm | DV
ShwPFon | Secondary Hot Water Pump Fail On Alarm | DV
ShwPFreq | Secondary Hot Water Pump Frequency | AO
ShwPFreq | Secondary Hot Water Pump Frequency | AV
ShwPKw | Secondary Hot Water Pump Kilowatts | AV
ShwPKwh | Secondary Hot Water Pump Kilowatt-Hours | AV
ShwPLclLoc | Secondary Hot Water Pump Local Lockout | DV
ShwPLclLocRst | Secondary Hot Water Pump Local Lockout Reset | DV
ShwPLd | Secondary Hot Water Pump Lead | AV
ShwPLg | Secondary Hot Water Pump Lag | AV
ShwPLgMan | Secondary Hot Water Pump Lag Manual | AV
ShwPMaintMd | Secondary Hot Water Pump Maintenance Mode | DV
ShwPMaintMdAlm | Secondary Hot Water Pump Maintenance Mode Alarm | DV
ShwPMaintReqAlm | Secondary Hot Water Pump Maintenance Request Alarm | DV
ShwPMaintReqRtRst | Secondary Hot Water Pump Maintenance Request Run Time Reset | DV
ShwPNumAvl | Number of Secondary Hot Water Pumps Available | AV
ShwPNumLclLoc | Number of Secondary Hot Water Pumps In Local Lockout | AV
ShwPNumOvrOn | Number of Secondary Hot Water Pumps Which Are Overridden On | AV
ShwPNumReq | Number of Secondary Hot Water Pumps Requested | AV
ShwPNumRun | Number of Secondary Hot Water Pumps Running | AV
ShwPOvrOn | Secondary Hot Water Pump Overridden On | DV
ShwPRotCmdTs | Secondary Hot Water Pump Rotation Command From Time Schedule | DV
ShwPRotOrdManValid | Secondary Hot Water Pump Manual Rotation Order Valid | DV
ShwPRotOrdValid | Secondary Hot Water Pump Rotation Order Valid | DV
ShwPRotSel | Secondary Hot Water Pump Rotation Selection | MV
ShwPRotSelfCor | Secondary Hot Water Pump Rotation Self Correcting Option | DV
ShwPRotSw | Secondary Hot Water Pump Rotation Switch | DV
ShwPRotTsRot | Secondary Hot Water Pump Rotation Time Schedule Force Rotation Option | DV
ShwPRt | Secondary Hot Water Pump Run Time | AV
ShwPRtRst | Secondary Hot Water Pump Run Time Reset | DV
ShwPSpd | Secondary Hot Water Pump Speed | AO
ShwPSpd | Secondary Hot Water Pump Speed | AV
ShwPSpdFbk | Secondary Hot Water Pump Speed Feedback | AI
ShwPSpdFbk | Secondary Hot Water Pump Speed Feedback | AV
ShwPSpdMin | Secondary Hot Water Pump Minimum Speed | AV
ShwPSts | Secondary Hot Water Pump Status | DI
ShwPSts | Secondary Hot Water Pump Status | DV
ShwPVfdAlm | Secondary Hot Water Pump Variable Frequency Drive Alarm | DI
ShwPVfdAlm | Secondary Hot Water Pump Variable Frequency Drive Alarm | DV
ShwPXrt | Secondary Hot Water Pump Extended Run Time | AV
ShwRFl | Secondary Hot Water Return Flow | AI
ShwRFl | Secondary Hot Water Return Flow | AV
ShwRFlCalAlm | Secondary Hot Water Return Flow Calibration Alarm | DI
ShwRFlCalAlm | Secondary Hot Water Return Flow Calibration Alarm | DV
ShwRPr | Secondary Hot Water Return Pressure | AI
ShwRPr | Secondary Hot Water Return Pressure | AV
ShwRTmp | Secondary Hot Water Return Temperature | AI
ShwRTmp | Secondary Hot Water Return Temperature | AV
ShwRTmpSpt | Secondary Hot Water Return Temperature Setpoint | AV
ShwSFl | Secondary Hot Water Supply Flow | AI
ShwSFl | Secondary Hot Water Supply Flow | AV
ShwSFlCalAlm | Secondary Hot Water Supply Flow Calibration Alarm | DI
ShwSFlCalAlm | Secondary Hot Water Supply Flow Calibration Alarm | DV
ShwSFlSpt | Secondary Hot Water Supply Flow Setpoint | AV
ShwSPr | Secondary Hot Water Supply Pressure | AI
ShwSPr | Secondary Hot Water Supply Pressure | AV
ShwSPrSpt | Secondary Hot Water Supply Pressure Setpoint | AV
ShwSTmp | Secondary Hot Water Supply Temperature | AI
ShwSTmp | Secondary Hot Water Supply Temperature | AV
ShwSTmpAlm | Secondary Hot Water Supply Temperature Alarm | DV
ShwSTmpAlmSv | Secondary Hot Water Supply Temperature Alarm Shunt Variable | DV
ShwSTmpSpt | Secondary Hot Water Supply Temperature Setpoint | AV
SlTmp | Suction Line Temperature | AI
SlTmp | Suction Line Temperature | AV
SmkAlm | Smoke Alarm | DI
SmkAlm | Smoke Alarm | DV
SmkAlmRst | Smoke Alarm Reset | DI
SmkAlmRst | Smoke Alarm Reset | DV
SmkDetAlm | Smoke Detector Alarm | DI
SmkDetAlm | Smoke Detector Alarm | DV
SmkEvacFanCmd | Smoke Evacuation Fan Command | DO
SmkEvacFanCmd | Smoke Evacuation Fan Command | DV
SmkEvacFanSts | Smoke Evacuation Fan Status | DI
SmkEvacFanSts | Smoke Evacuation Fan Status | DV
SmkPrgFanAmpFalm | Smoke Purge Fan Amp Fail Alarm | DV
SmkPrgFanCmd | Smoke Purge Fan Command | DO
SmkPrgFanCmd | Smoke Purge Fan Command | DV
SmkPrgFanOvr | Smoke Purge Fan Override | DV
SmkPrgFanSts | Smoke Purge Fan Status | DI
SmkPrgFanSts | Smoke Purge Fan Status | DV
SmkWinCmd | Smoke Window Command | DO
SmkWinCmd | Smoke Window Command | DV
SmkWinSts | Smoke Window Status | DI
SmkWinSts | Smoke Window Status | DV
SmpLkFalm | Sump Leak Fail Alarm | DV
SmrMd | Summer Mode | DV
SmrWntrMd | Summer/Winter Mode | DV
SpFanAmpFalm | Stair Pressurization Fan Amp Fail Alarm | DV
SpFanCmd | Stair Pressurization Fan Command | DO
SpFanCmd | Stair Pressurization Fan Command | DV
SpFanOvr | Stair Pressurization Fan Override | DV
SpFanSts | Stair Pressurization Fan Status | DI
SpFanSts | Stair Pressurization Fan Status | DV
SstmFl | Secondary Steam Flow | AI
SstmFl | Secondary Steam Flow | AV
SstmPr | Secondary Steam Pressure | AI
SstmPr | Secondary Steam Pressure | AV
SstmPrSpt | Secondary Steam Pressure Setpoint | AV
SstmSTmp | Secondary Steam Supply Temperature | AI
SstmSTmp | Secondary Steam Supply Temperature | AV
SstmSTmpSpt | Secondary Steam Supply Temperature Setpoint | AV
StbMd | Standby Mode | DV
StbTm | Standby Time | AV
StmBlrGasFlMain | Main Hot Water Boiler Gas Flow | AI
StmBlrGasFlMain | Main Hot Water Boiler Gas Flow | AV
StmCost | Steam Cost | AV
StmFl | Steam Flow | AI
StmFl | Steam Flow | AV
StmHxEna | Steam Heat Exchanger Enable | DV
StmHxHwBypVlvFalm | Steam Heat Exchanger Hot Water Bypass Valve Failure Alarm | DV
StmHxHwBypVlvFbk | Steam Heat Exchanger Bypass Valve Feedback | AI
StmHxHwBypVlvFbk | Steam Heat Exchanger Bypass Valve Feedback | AV
StmHxHwBypVlvPos | Steam Heat Exchanger Bypass Valve Position | AO
StmHxHwBypVlvPos | Steam Heat Exchanger Bypass Valve Position | AV
StmHxHwDifPr | Steam Heat Exchanger Hot Water Differential Pressure | AI
StmHxHwDifPr | Steam Heat Exchanger Hot Water Differential Pressure | AV
StmHxHwFl | Steam Heat Exchanger Hot Water Flow | AI
StmHxHwFl | Steam Heat Exchanger Hot Water Flow | AV
StmHxHwFlSpt | Steam Heat Exchanger Hot Water Flow Setpoint | AV
StmHxHwRIsoVlvCmd | Steam Heat Exchanger Hot Water Return Isolation Valve Command | DO
StmHxHwRIsoVlvCmd | Steam Heat Exchanger Hot Water Return Isolation Valve Command | DV
StmHxHwRIsoVlvCmdCls | Steam Heat Exchanger Hot Water Return Isolation Valve Close Command | DO
StmHxHwRIsoVlvCmdCls | Steam Heat Exchanger Hot Water Return Isolation Valve Close Command | DV
StmHxHwRIsoVlvCmdOpn | Steam Heat Exchanger Hot Water Return Isolation Valve Open Command | DO
StmHxHwRIsoVlvCmdOpn | Steam Heat Exchanger Hot Water Return Isolation Valve Open Command | DV
StmHxHwRIsoVlvEsw | Steam Heat Exchanger Hot Water Return Isolation Valve End Switch | DI
StmHxHwRIsoVlvEsw | Steam Heat Exchanger Hot Water Return Isolation Valve End Switch | DV
StmHxHwRIsoVlvEswCls | Steam Heat Exchanger Hot Water Return Isolation Valve Closed End Switch | DI
StmHxHwRIsoVlvEswCls | Steam Heat Exchanger Hot Water Return Isolation Valve Closed End Switch | DV
StmHxHwRIsoVlvEswOpn | Steam Heat Exchanger Hot Water Return Isolation Valve Open End Switch | DI
StmHxHwRIsoVlvEswOpn | Steam Heat Exchanger Hot Water Return Isolation Valve Open End Switch | DV
StmHxHwRIsoVlvFalm | Steam Heat Exchanger Hot Water Return Isolation Valve Failure Alarm | DV
StmHxHwRIsoVlvFbk | Steam Heat Exchanger Hot Water Return Isolation Valve Feedback | AI
StmHxHwRIsoVlvFbk | Steam Heat Exchanger Hot Water Return Isolation Valve Feedback | AV
StmHxHwRIsoVlvFcls | Steam Heat Exchanger Hot Water Return Isolation Valve Fail Closed Alarm | DV
StmHxHwRIsoVlvFopn | Steam Heat Exchanger Hot Water Return Isolation Valve Fail Open Alarm | DV
StmHxHwRIsoVlvPos | Steam Heat Exchanger Hot Water Return Isolation Valve Position | AO
StmHxHwRIsoVlvPos | Steam Heat Exchanger Hot Water Return Isolation Valve Position | AV
StmHxHwRTmp | Steam Heat Exchanger Hot Water Return Temperature | AI
StmHxHwRTmp | Steam Heat Exchanger Hot Water Return Temperature | AV
StmHxHwSFl | Steam Heat Exchanger Hot Water Supply Flow | AI
StmHxHwSFl | Steam Heat Exchanger Hot Water Supply Flow | AV
StmHxHwSFlSpt | Steam Heat Exchanger Hot Water Supply Flow Setpoint | AV
StmHxHwSIsoVlvCmd | Steam Heat Exchanger Hot Water Supply Isolation Valve Command | DO
StmHxHwSIsoVlvCmd | Steam Heat Exchanger Hot Water Supply Isolation Valve Command | DV
StmHxHwSIsoVlvCmdCls | Steam Heat Exchanger Hot Water Supply Isolation Valve Close Command | DO
StmHxHwSIsoVlvCmdCls | Steam Heat Exchanger Hot Water Supply Isolation Valve Close Command | DV
StmHxHwSIsoVlvCmdOpn | Steam Heat Exchanger Hot Water Supply Isolation Valve Open Command | DO
StmHxHwSIsoVlvCmdOpn | Steam Heat Exchanger Hot Water Supply Isolation Valve Open Command | DV
StmHxHwSIsoVlvEsw | Steam Heat Exchanger Hot Water Supply Isolation Valve End Switch | DI
StmHxHwSIsoVlvEsw | Steam Heat Exchanger Hot Water Supply Isolation Valve End Switch | DV
StmHxHwSIsoVlvEswCls | Steam Heat Exchanger Hot Water Supply Isolation Valve Closed End Switch | DI
StmHxHwSIsoVlvEswCls | Steam Heat Exchanger Hot Water Supply Isolation Valve Closed End Switch | DV
StmHxHwSIsoVlvEswOpn | Steam Heat Exchanger Hot Water Supply Isolation Valve Open End Switch | DI
StmHxHwSIsoVlvEswOpn | Steam Heat Exchanger Hot Water Supply Isolation Valve Open End Switch | DV
StmHxHwSIsoVlvFalm | Steam Heat Exchanger Hot Water Supply Isolation Valve Failure Alarm | DV
StmHxHwSIsoVlvFbk | Steam Heat Exchanger Hot Water Supply Isolation Valve Feedback | AI
StmHxHwSIsoVlvFbk | Steam Heat Exchanger Hot Water Supply Isolation Valve Feedback | AV
StmHxHwSIsoVlvFcls | Steam Heat Exchanger Hot Water Supply Isolation Valve Fail Closed Alarm | DV
StmHxHwSIsoVlvFopn | Steam Heat Exchanger Hot Water Supply Isolation Valve Fail Open Alarm | DV
StmHxHwSIsoVlvPos | Steam Heat Exchanger Hot Water Supply Isolation Valve Position | AO
StmHxHwSIsoVlvPos | Steam Heat Exchanger Hot Water Supply Isolation Valve Position | AV
StmHxHwSTmp | Steam Heat Exchanger Hot Water Supply Temperature | AI
StmHxHwSTmp | Steam Heat Exchanger Hot Water Supply Temperature | AV
StmHxHwSTmpAlm | Steam Heat Exchanger How Water Supply Temperature Alarm | DV
StmHxHwSTmpAlmSv | Steam Heat Exchanger How Water Supply Temperature Alarm Shunt Variable | DV
StmHxHwSTmpSpt | Steam Heat Exchanger Hot Water Supply Temperature Setpoint | AV
StmHxLclLoc | Steam Heat Exchanger Local Lockout | DV
StmHxLclLocRst | Steam Heat Exchanger Local Lockout Reset | DV
StmHxLd | Steam Heat Exchanger Lead | AV
StmHxLdMan | Steam Heat Exchanger Lead Manual | AV
StmHxLg | Steam Heat Exchanger Lag | AV
StmHxLgMan | Steam Heat Exchanger Lag Manual | AV
StmHxMaintMd | Steam Heat Exchanger Maintenance Mode | DV
StmHxMaintMdAlm | Steam Heat Exchanger Maintenance Mode Alarm | DV
StmHxMaintReqAlm | Steam Heat Exchanger Maintenance Request Alarm | DV
StmHxMaintReqRtRst | Steam Heat Exchanger Maintenance Request Run Time Reset | DV
StmHxNumAvl | Number of Steam Heat Exchangers Available | AV
StmHxNumLclLoc | Number of Steam Heat Exchangers In Local Lockout | AV
StmHxNumOvrOn | Number of Steam Heat Exchangers Which Are Overridden On | AV
StmHxNumReq | Number of Steam Heat Exchangers Requested | AV
StmHxNumRun | Number of Steam Heat Exchangers Running | AV
StmHxOvrOn | Steam Heat Exchanger Overridden On | DV
StmHxRotCmdTs | Steam Heat Exchanger Rotation Command From Time Schedule | DV
StmHxRotOrdManValid | Steam Heat Exchanger Manual Rotation Order Valid | DV
StmHxRotOrdValid | Steam Heat Exchanger Rotation Order Valid | DV
StmHxRotSel | Steam Heat Exchanger Rotation Selection | MV
StmHxRotSelfCor | Steam Heat Exchanger Rotation Self Correcting Option | DV
StmHxRotSw | Steam Heat Exchanger Rotation Switch | DV
StmHxRotTsRot | Steam Heat Exchanger Rotation Time Schedule Force Rotation Option | DV
StmHxRt | Steam Heat Exchanger Run Time | AV
StmHxRtRst | Steam Heat Exchanger Run Time Reset | DV
StmHxStgActvCapDsn | Steam Heat Exchanger Active Stage Design Capacity | AV
StmHxStgActvCapMin | Steam Heat Exchanger Active Stage Minimum Capacity | AV
StmHxStgActvFlMin | Steam Heat Exchanger Active Stage Minimum Flow | AV
StmHxStgNxtCapDsn | Steam Heat Exchanger Next Stage Design Capacity | AV
StmHxStgNxtCapMin | Steam Heat Exchanger Next Stage Minimum Capacity | AV
StmHxStgNxtFlMin | Steam Heat Exchanger Next Stage Minimum Flow | AV
StmHxStgPrvCapDsn | Steam Heat Exchanger Previous Stage Design Capacity | AV
StmHxStgPrvCapMin | Steam Heat Exchanger Previous Stage Minimum Capacity | AV
StmHxStgPrvFlMin | Steam Heat Exchanger Previous Stage Minimum Flow | AV
StmHxStgSpt | Steam Heat Exchanger Staging Setpoint | AV
StmHxStm13VlvFalm | Steam Heat Exchanger Steam One Third Valve Fail Alarm | DV
StmHxStm13VlvFbk | Steam Heat Exchanger Steam One Third Valve Feedback | AI
StmHxStm13VlvFbk | Steam Heat Exchanger Steam One Third Valve Feedback | AV
StmHxStm13VlvPos | Steam Heat Exchanger Steam One Third Valve Position | AO
StmHxStm13VlvPos | Steam Heat Exchanger Steam One Third Valve Position | AV
StmHxStm23VlvFalm | Steam Heat Exchanger Steam Two Third Valve Fail Alarm | DV
StmHxStm23VlvFbk | Steam Heat Exchanger Steam Two Third Valve Feedback | AI
StmHxStm23VlvFbk | Steam Heat Exchanger Steam Two Third Valve Feedback | AV
StmHxStm23VlvPos | Steam Heat Exchanger Steam Two Third Valve Position | AO
StmHxStm23VlvPos | Steam Heat Exchanger Steam Two Third Valve Position | AV
StmHxStmFl | Steam Heat Exchanger Steam Flow | AI
StmHxStmFl | Steam Heat Exchanger Steam Flow | AV
StmHxStmIsoVlvCmd | Steam Heat Exchanger Steam Isolation Valve Command | DO
StmHxStmIsoVlvCmd | Steam Heat Exchanger Steam Isolation Valve Command | DV
StmHxStmIsoVlvEsw | Steam Heat Exchanger Steam Isolation Valve End Switch | DI
StmHxStmIsoVlvEsw | Steam Heat Exchanger Steam Isolation Valve End Switch | DV
StmHxStmIsoVlvEswCls | Steam Heat Exchanger Steam Isolation Valve Closed End Switch | DI
StmHxStmIsoVlvEswCls | Steam Heat Exchanger Steam Isolation Valve Closed End Switch | DV
StmHxStmIsoVlvEswOpn | Steam Heat Exchanger Steam Isolation Valve Open End Switch | DI
StmHxStmIsoVlvEswOpn | Steam Heat Exchanger Steam Isolation Valve Open End Switch | DV
StmHxStmIsoVlvFcls | Steam Heat Exchanger Steam Isolation Valve Fail Closed Alarm | DV
StmHxStmIsoVlvFopn | Steam Heat Exchanger Steam Isolation Valve Fail Open Alarm | DV
StmHxXrt | Steam Heat Exchanger Extended Run Time | AV
StmPr | Steam Pressure | AI
StmPr | Steam Pressure | AV
StmSPr | Steam Supply Pressure | AI
StmSPr | Steam Supply Pressure | AV
StmSTmp | Steam Supply Temperature | AI
StmSTmp | Steam Supply Temperature | AV
StmSVlvFbk | Steam Supply Valve Feedback | AI
StmSVlvFbk | Steam Supply Valve Feedback | AV
StmSVlvPos | Steam Supply Valve Position | AO
StmSVlvPos | Steam Supply Valve Position | AV
StmVlv1Pos | Steam 1/3 Control Valve Position | AO
StmVlv1Pos | Steam 1/3 Control Valve Position | AV
StmVlv2Pos | Steam 2/3 Control Valve Position | AO
StmVlv2Pos | Steam 2/3 Control Valve Position | AV
StmVlvFbk | Steam Valve Feedback | AI
StmVlvFbk | Steam Valve Feedback | AV
StmVlvPos | Steam Valve Position | AO
StmVlvPos | Steam Valve Position | AV
StmWgt | Steam Weight | AV
StPrAlm | Static Pressure Alarm | DI
StPrAlm | Static Pressure Alarm | DV
StPrFalm | Static Pressure Fail Alarm | DV
StPrHalm | Static Pressure High Alarm | DV
StPrHalmSv | Static Pressure High Alarm Shunt Variable | DV
StPrLalm | Static Pressure Low Alarm | DV
StPrRstReq | Static Pressure Reset Requests | AV
StPrRstReqHalm | Static Pressure Reset Request High Alarm | DV
StPrRstReqHalmSv | Static Pressure Reset Request High Alarm Shunt Variable | DV
StPrRstReqPct | Static Pressure Reset Request Hours as Percent | AV
StPrRstReqRst | Static Pressure Reset Request Hours Reset | DV
StPrRstReqRt | Static Pressure Reset Request Hours | AV
SttCalEna | Stroke Time Calibration Enable | DV
SysMd | System Mode | MV
SysMdEff | Effective System Mode | MV
SysRunHlmt | System Running High Limit Setpoint | AV
SysRunRt | System Running Run Time | AV
TesChrgMd | Thermal Energy Storage Charge | DV
TesDchrgMd | Thermal Energy Storage Discharge Mode | DV
TesFl | Thermal Energy Storage Flow | AI
TesFl | Thermal Energy Storage Flow | AV
TesRTmp | Thermal Energy Storage Return Temperature | AI
TesRTmp | Thermal Energy Storage Return Temperature | AV
TesSTmp | Thermal Energy Storage Supply Temperature | AI
TesSTmp | Thermal Energy Storage Supply Temperature | AV
TestDly | Test Delay | AV
TfrFanAmpFalm | Transfer Fan Amp Fail Alarm | DV
TfrFanCmd | Transfer Fan Command | DO
TfrFanCmd | Transfer Fan Command | DV
TfrFanOvr | Transfer Fan Override | DV
TfrFanSts | Transfer Fan Status | DI
TfrFanSts | Transfer Fan Status | DV
TmaVntClsTml | Time-Averaged Close Time Left | AV
TmaVntOpnTml | Time-Averaged Open Time Left | AV
TmaVntSts | Time-Averaged Ventilation Status | DV
TmpLlmtAlm | Temperature Low Limit Alarm | DI
TmpLlmtAlm | Temperature Low Limit Alarm | DV
TmpLlmtAlmRst | Temperature Low Limit Alarm Reset | DV
TnkHdrTmp | Tank Header Temperature | AI
TnkHdrTmp | Tank Header Temperature | AV
TnkIsoVlvPos | Tank Isolation Valve Position | AO
TnkIsoVlvPos | Tank Isolation Valve Position | AV
TnkRTmp | Tank Return Temperature | AI
TnkRTmp | Tank Return Temperature | AV
TnkTmp | Tank Temperature | AI
TnkTmp | Tank Temperature | AV
TsBlrRot | Boiler Rotation Time Schedule | DV
TsChRot | Chiller Rotation Time Schedule | DV
TsChwHxRot | Chilled Water Heat Exchanger Rotation Time Schedule | DV
TsCtRot | Cooling Tower Rotation Time Schedule | DV
TsCwPRot | Condenser Water Pump Rotation Time Schedule | DV
TsGblNxtTm | Global Time Schedule Time to Next Transition | AV
TsGblNxtVal | Global Time Schedule Next Value | DV
TsGblOccCmd | Global Time Schedule Occupancy Command | DV
TsLcl | Local Time Schedule | DV
TsLclNxtTm | Local Time Schedule Time to Next Transition | AV
TsLclNxtVal | Local Time Schedule Next Value | DV
TsLclOccCmd | Local Time Schedule Occupancy Command | DV
TsNxtTm | Time Schedule Time to Next Transition | AV
TsNxtVal | Time Schedule Next Value | DV
TsPchwPRot | Primary Chilled Water Pump Rotation Time Schedule | DV
TsPhwPRot | Primary Hot Water Pump Rotation Time Schedule | DV
TsSchwPRot | Secondary Chilled Water Pump Rotation Time Schedule | DV
TsShwPRot | Secondary Hot Water Pump Rotation Time Schedule | DV
TsStmHxRot | Steam Heat Exchanger Rotation Time Schedule | DV
UhCmd | Unit Heater Command | DO
UhCmd | Unit Heater Command | DV
UhSts | Unit Heater Status | DI
UhSts | Unit Heater Status | DV
UnitCph | Unit Cycles per Hour | AV
UnitEna | Unit Enable | DV
UnitLoc | Unit Lockout | DV
UnocDon | Occupied to Unoccupied Delay | AV
UvLtCmd | UV Light Command | DO
UvLtCmd | UV Light Command | DV
UvLtSts | UV Light Status | DI
UvLtSts | UV Light Status | DV
VavAirFl | VAV Air Flow | AI
VavAirFl | VAV Air Flow | AV
VavAirFlPctMax | VAV Maximum Air Flow Percent | AV
VavAirFlSptBldgDsn | VAV Air Flow Design Minimum Building Setpoint | AO
VavAirFlSptBldgDsn | VAV Air Flow Design Minimum Building Setpoint | AV
VavAirFlSptBldgTot | VAV Air Flow Minimum Building Setpoint Total | AO
VavAirFlSptBldgTot | VAV Air Flow Minimum Building Setpoint Total | AV
VavAirFlSptOccTot | VAV Air Flow Minimum Occupancy Setpoint Total | AO
VavAirFlSptOccTot | VAV Air Flow Minimum Occupancy Setpoint Total | AV
VavAirFlSptVntMinTot | VAV Air Flow Ventilation Minimum Setpoint Total | AO
VavAirFlSptVntMinTot | VAV Air Flow Ventilation Minimum Setpoint Total | AV
VavAirFlTot | VAV Total Air Flow | AV
VavDprPos | VAV Damper Position | AO
VavDprPos | VAV Damper Position | AV
VavDprPosAvg | Average VAV Damper Position | AV
VavDprPosHi | Highest VAV Damper Position | AV
VavDprPosLo | Lowest VAV Damper Position | AV
VavFanCmd | VAV Fan Command | DO
VavFanCmd | VAV Fan Command | DV
VavFireCnt | VAV Fire Count | AV
VavFzSbIgnReq | VAV Freeze Setback Ignored Requests | AV
VavFzSbReq | VAV Freeze Setback Requests | AV
VavHvacMd | VAV HVAC Mode | MV
VavOccClgCnt | VAV Occupied Cooling Count | AV
VavOccCnt | VAV Occupied Count | AV
VavOccHtgCnt | VAV Occupied Heating Count | AV
VavOccOvrIgnReq | VAV Occupancy Override Ignored Requests | AV
VavOccOvrReq | VAV Occupancy Override Requests | AV
VavOffCnt | VAV Off Count | AV
VavOvrCnt | VAV Override Count | AV
VavRmCO2Avg | VAV Average Room Carbon Dioxide | AV
VavRmCO2Hi | VAV Highest Room Carbon Dioxide | AV
VavRmCO2Lo | VAV Lowest Room Carbon Dioxide | AV
VavRmRhAvg | VAV Average Room Relative Humidity | AV
VavRmRhHi | VAV Highest Room Relative Humidity | AV
VavRmRhLo | VAV Lowest Room Relative Humidity | AV
VavRmTmpAvg | VAV Average Room Temperature | AV
VavRmTmpClg | VAV Cooling Room Temperature | AV
VavRmTmpHi | VAV Highest Room Temperature | AV
VavRmTmpHtg | VAV Heating Room Temperature | AV
VavRmTmpLo | VAV Lowest Room Temperature | AV
VavRmTmpSptClg | VAV Room Temperature Cooling Setpoint | AV
VavRmTmpSptHtg | VAV Room Temperature Heating Setpoint | AV
VavRmTmpSptSbAvg | VAV Average Room Temperature Setback Setpoint | AV
VavRmTmpSptSuAvg | VAV Average Room Temperature Setup Setpoint | AV
VavSaStPrSptRstReq | VAV Supply Air Static Pressure Setpoint Reset Requests | AV
VavSaTmpSptRstReq | VAV Supply Air Temperature Setpoint Reset Requests | AV
VavSbIgnReq | VAV Setback Ignored Requests | AV
VavSbReq | VAV Setback Requests | AV
VavStsCnt | VAV Controller Status Count | AV
VavSuIgnReq | VAV Setup Ignored Requests | AV
VavSuReq | VAV Setup Requests | AV
VavTestStg | VAV Test Stage | MV
VavTlAvg | VAV Average Terminal Load | AV
VavTlHi | VAV Highest Terminal Load | AV
VavTlLo | VAV Lowest Terminal Load | AV
VavUnocCnt | VAV Unoccupied Count | AV
VavVntFlPctMax | VAV Maximum Ventilation Flow Percentage | AO
VavVntFlPctMax | VAV Maximum Ventilation Flow Percentage | AV
VavZnGrpMd | VAV Zone Group Mode | MV
VelPr | Velocity Pressure | AI
VelPr | Velocity Pressure | AV
VelPrMin | Velocity Pressure Minimum | AV
VelPrRated | Rated Velocity Pressure | AV
VelPrTestSts | Velocity Pressure Test Stage | MV
VibSwSts | Vibration Switch Status | DI
VibSwSts | Vibration Switch Status | DV
VntLoad | Ventilation Load | AV
WdRmCO2 | Wireless Device Room Carbon Dioxide | AI
WdRmCO2 | Wireless Device Room Carbon Dioxide | AV
WdRmCO2 | Wireless Device Room Carbon Dioxide | SS
WdRmRh | Wireless Device Room Relative Humidity | AI
WdRmRh | Wireless Device Room Relative Humidity | AV
WdRmRh | Wireless Device Room Relative Humidity | SS
WdRmTmp | Wireless Device Room Temperature | AI
WdRmTmp | Wireless Device Room Temperature | AV
WdRmTmp | Wireless Device Room Temperature | SS
WinSw | Window Switch | DI
WinSw | Window Switch | DV
WntrMd | Winter Mode | DV
WsHpSTmp | Water Source Heat Pump Supply Water Temperature | AI
WsHpSTmp | Water Source Heat Pump Supply Water Temperature | AV
ZnAirFl | Zone Air Flow | AI
ZnAirFl | Zone Air Flow | AV
ZnAirFlPctMax | Zone Maximum Air Flow Percent | AV
ZnAirFlSptBldgDsn | Zone Air Flow Design Minimum Building Setpoint | AO
ZnAirFlSptBldgDsn | Zone Air Flow Design Minimum Building Setpoint | AV
ZnAirFlSptBldgTot | Zone Air Flow Minimum Building Setpoint Total | AO
ZnAirFlSptBldgTot | Zone Air Flow Minimum Building Setpoint Total | AV
ZnAirFlSptOccTot | Zone Air Flow Minimum Occupancy Setpoint Total | AO
ZnAirFlSptOccTot | Zone Air Flow Minimum Occupancy Setpoint Total | AV
ZnAirFlSptVntMinTot | Zone Air Flow Ventilation Minimum Setpoint Total | AO
ZnAirFlSptVntMinTot | Zone Air Flow Ventilation Minimum Setpoint Total | AV
ZnAirFlTot | Zone Total Air Flow | AV
ZnCdDprPos | Zone Cold Deck Damper Position | AO
ZnCdDprPos | Zone Cold Deck Damper Position | AV
ZnChwVlvPosAvg | Average Zone Chilled Water Valve Position | AV
ZnChwVlvPosHi | Most Open Zone Chilled Water Valve Position | AV
ZnChwVlvPosHiDz | Most Open Zone Chilled Water Valve Position Dead Zone | AV
ZnChwVlvPosHiSpt | Most Open Zone Chilled Water Valve Position Setpoint | AV
ZnChwVlvPosLo | Minimum Zone Chilled Water Valve Position | AV
ZnClgEna | Zone Cooling Enable | DO
ZnClgEna | Zone Cooling Enable | DV
ZnCO | Zone Carbon Monoxide | AI
ZnCO | Zone Carbon Monoxide | AV
ZnCO2 | Zone Carbon Dioxide | AI
ZnCO2 | Zone Carbon Dioxide | AV
ZnCO2 | Zone Carbon Dioxide | SS
ZnDew | Zone Dew Point | AI
ZnDew | Zone Dew Point | AV
ZnDprFbk | Zone Damper Feedback | AO
ZnDprFbk | Zone Damper Feedback | AV
ZnDprFbkAvg | Average Zone Damper Feedback | AV
ZnDprFbkHi | Highest Zone Damper Feedback | AV
ZnDprFbkLo | Lowest Zone Damper Feedback | AV
ZnDprPos | Zone Damper Position | AO
ZnDprPos | Zone Damper Position | AV
ZnDprPosAvg | Average Zone Damper Position | AV
ZnDprPosHi | Highest Zone Damper Position | AV
ZnDprPosLo | Lowest Zone Damper Position | AV
ZnEna | Zone Unit Enable | DO
ZnEna | Zone Unit Enable | DV
ZnFzSbIgnReq | Zone Freeze Setback Ignored Requests | AV
ZnFzSbReq | Zone Freeze Setback Requests | AV
ZnHdDprPos | Zone Hot Deck Damper Position | AO
ZnHdDprPos | Zone Hot Deck Damper Position | AV
ZnHtgEna | Zone Heating Enable | DO
ZnHtgEna | Zone Heating Enable | DV
ZnHvacMd | Zone HVAC Mode | MV
ZnNO2 | Zone Nitrogen Dioxide | AI
ZnNO2 | Zone Nitrogen Dioxide | AV
ZnO2 | Zone Oxygen | AI
ZnO2 | Zone Oxygen | AV
ZnOccCmd | Zone Occupancy Command | MV
ZnOccOvr | Zone Occupancy Override | DI
ZnOccOvr | Zone Occupancy Override | DV
ZnOccOvr | Zone Occupancy Override | SS
ZnOccOvrIgnReq | Zone Occupancy Override Ignored Requests | AV
ZnOccOvrReq | Zone Occupancy Override Requests | AV
ZnRaTmp | Zone Return Air Temperature | AI
ZnRaTmp | Zone Return Air Temperature | AV
ZnRh | Zone Relative Humidity | AI
ZnRh | Zone Relative Humidity | AV
ZnRh | Zone Relative Humidity | SS
ZnRhtVlvCmd | Zone Reheat Valve Command | DO
ZnRhtVlvCmd | Zone Reheat Valve Command | DV
ZnRhtVlvPos | Zone Reheat Valve Position | AO
ZnRhtVlvPos | Zone Reheat Valve Position | AV
ZnRmCO2Avg | Zone Average Room Carbon Dioxide | AV
ZnRmCO2Hi | Zone Highest Room Carbon Dioxide | AV
ZnRmCO2Lo | Zone Lowest Room Carbon Dioxide | AV
ZnRmRhAvg | Zone Average Room Relative Humidity | AV
ZnRmRhHi | Zone Highest Room Relative Humidity | AV
ZnRmRhLo | Zone Lowest Room Relative Humidity | AV
ZnRmTmpAvg | Zone Average Room Temperature | AV
ZnRmTmpClg | Zone Cooling Room Temperature | AV
ZnRmTmpHi | Zone Highest Room Temperature | AV
ZnRmTmpHtg | Zone Heating Room Temperature | AV
ZnRmTmpLo | Zone Lowest Room Temperature | AV
ZnRmTmpSptClg | Zone Room Temperature Cooling Setpoint | AV
ZnRmTmpSptHtg | Zone Room Temperature Heating Setpoint | AV
ZnRmTmpSptSbAvg | Zone Average Room Temperature Setback Setpoint | AV
ZnRmTmpSptSuAvg | Zone Average Room Temperature Setup Setpoint | AV
ZnSaStPrSptRstReq | Zone Supply Air Static Pressure Setpoint Reset Requests | AV
ZnSaTmp | Zone Supply Air Temperature | AI
ZnSaTmp | Zone Supply Air Temperature | AV
ZnSaTmpSptRstReq | Zone Supply Air Temperature Setpoint Reset Requests | AV
ZnSbIgnReq | Zone Setback Ignored Requests | AV
ZnSbReq | Zone Setback Requests | AV
ZnStmVlvPos | Zone Steam Valve Position | AO
ZnStmVlvPos | Zone Steam Valve Position | AV
ZnStsCnt | Zone Controller Status Count | AV
ZnSuIgnReq | Zone Setup Ignored Requests | AV
ZnSuReq | Zone Setup Requests | AV
ZnTmp | Zone Temperature | AI
ZnTmp | Zone Temperature | AV
ZnTmp | Zone Temperature | SS
ZnTmpSpt | Zone Temperature Setpoint | AV
ZnTmpSptAdj | Zone Temperature Setpoint Adjustment | AI
ZnTmpSptAdj | Zone Temperature Setpoint Adjustment | AV
ZnTmpSptAdj | Zone Temperature Setpoint Adjustment | SS
ZnTmpSptClg | Zone Temperature Cooling Setpoint | AV
ZnTmpSptHtg | Zone Temperature Heating Setpoint | AV
ZnVdPos | Zone Volume Damper Position | AO
ZnVdPos | Zone Volume Damper Position | AV
ZnVntFlPctMax | Zone Maximum Ventilation Flow Percentage | AO
ZnVntFlPctMax | Zone Maximum Ventilation Flow Percentage | AV